###### Answers to "technical" clarification questions

Subject: AOI N° 06 / CMI/ 2025 for project for the design, supply and execution of the construction works of the SUD 33/15 kV and NORD 33/15 kV substations, as well as the rehabilitation of six existing substations in the city of Nouakchott in a single lot.

Complements to the technical specifications

- Technical Specifications Auxiliary Services Transformer,

- Technical Specifications of 15 kV Cables,

- Specifications of the 15 kV and 33 kV insulators and insolent columns,

- Technical specifications Surge protectors,

- Technical specifications Grounding system,

- Technical specifications for switching and 400 Vac switchboard,

- Technical specifications Lighting and power socket,

- Technical Specifications Auxiliary Services Transformer,

- Technical specifications Fiber cables,

- Technical Specifications of Gates and Wicket Gates,

## Technical Specification – Ancillary Services Transformers (ASTs) 15/0.41 kV – 100 kVA

##### OBJECT

Define the technical, normative and functional requirements applicable to the transformers of auxiliary services (TSA) intended to supply the AC auxiliaries of the 33/15 kV substations of Nouakchott.

##### REFERENCE STANDARDS

- IEC 60076 : Power Transformers (All Relevant Parts)

- DIN 42 500 / VDE 0532 / NF C 52-100 / NF C 52-113 : Equivalent national standards

- IEC 60071-2 : Isolation Coordination – Leakage Distances

- IEC 60332-3, IEC 61034, IEC 60754 : Fire behaviour of cables

- IEC 60076-11 : Testing of Oil-Immersed Power Transformers

##### KEY FEATURES

| Characteristic | Requirement / Value |
| --- | --- |
| Type | Hermetic full fill, radiator tank, outdoor service |
| Rated power | 100 kVA |
| Number of Phases/Windings | 3 / 2 |
| Assigned voltages | MV: 15 kV / LV: 0.41 kV |
| Assigned Frequency | 50 Hz |
| Cooling | ONAN |
| Max. Insulation Temperature | 155°C (Class F) |
| Max. warm-up to In | 100 K |

| Characteristic | Requirement / Value |
| --- | --- |
| Coupling / Phase shift | Dyn11 |
| Short-circuit impedance | 4% (base 100 kVA) |
| Tap changer | Power off, ±2.5% per position, 5 positions |
| Windings | Copper, epoxy insulation |
| Magnetic circuit | Grain-oriented sheet, cold-rolled, 0.23–0.30 mm thick, induction ≤ 1.7 T |
| MV bushings (primary) | Branch Lines 15 kV / 250 A |
| LV terminals (secondary) | Porcelain 1 kV / 250 A, protective metal cover |
| Nameplate | IEC 60076-1 compliant, complete and indelible data |
| Corrosion protection | Complies with the General Technical Conditions |
| Track Rollers | 4, 2-axis swivel |
| Lifting Rings | 2 minimum |
| Vat | Variable volume, waterproof, bolt-on lid, water drain |
| Fire-resistant retention tank | Required for installation |

- CONSTRUCTION REQUIREMENTS

###### Magnetic circuit

    - Stacking of cold-rolled grain-oriented sheet metal.

    - Carlite insulation, high permeability, low losses.

    - Strong, bolt-free assembly to withstand the stresses of short circuit and transport.

###### Windings

    - Made of copper, slab or strip type according to the manufacturer's choice.

    - Rigid assembly, anti-deformation wedging, connections maintained.

    - Main insulation by hot-cast and vacuum-cast epoxy resin.

###### Connection terminals

    - Resistant to mechanical and electrodynamic forces.

    - Min. creepage 31 mm/kV (Class IV IEC 60071-2).

###### Tap changer

    - Power off type, clear location marking.

    - Locking plate with lock.

###### Cooling system

    - Free Oil Cooling (ONAN).

##### PROTECTIONS AND INSTRUMENTATION

###### Multifunction protection relays (DSP type)

- PT100 probes on each HVA and LV winding, connected to a thermal protection relay:

  - 1st stage: alarm

  - 2nd stage: induction

###### Control-Command Interface :

  - Terminals (dry contact) for alarms and thermal triggering

  - Analogue measurements (HVA/LV temperatures) available via communication

- Probe Wiring : suitable for high temperatures, IEC compliant (halogen-free, non-fire spreading, low smoke/corrosiveness), indelible marking.

##### INSTALLATION

- Positioning on concrete slab with fire-resistant retention tank.

- HVA connection via 95 mm² single-core PRC cables, LV connection to TR box and switcher.

- Grounded cable trays.

- Connection of metal masses and cable screens to the substation's earth network.

- Installation of BT TR enclosures near each TSA.

- Marking in accordance with the nomenclature and electrical diagrams.

##### IDENTIFICATION

- Complete and indelible nameplate, in French, IEC 60076-1 compliant.

- Supplier plate.

##### CONTROL-COMMAND INTERFACE

- Provision of the following information:

  - Winding temperature (alarm, trigger)

  - Analogue measurements (HVA/LV temperatures) by communication protocol compatible with the substation system.

##### TESTING AND QUALIFYING

- Individual series tests : IEC 60076-11 compliant on each transformer.

- Type Tests : Heating test on each type; PV of tests of equivalent type to be provided for the other tests.

- Special tests : Measurement of the noise level on each transformer.

##### DOCUMENTATION TO BE PROVIDED

- Technical data sheets and certificates of conformity

- Design calculation notes (power, heating, impedance)

- Factory and type test reports

- Installation and connection diagrams

- Device and cable tracking plan

##### SERVICES OF THE CONTRACTOR

- Supply and installation of 4 TSAs (2 per SUD and DUAL substation)

- Installation on concrete slab and retention tank

- Installation and connection of LV TR boxes

- Installation and connection of HVA and LV cables, end accessories

- Grounding of metal masses and screens

- Identification and complete documentation

###### Remark:

Any synthetic insulation containing polychlorinated biphenyls (PCBs, Askarel) is strictly prohibited.

## Technical Specification of 15 kV Cables for 33/15 kV Substations in Nouakchott

###### Object

This specification defines the technical, constructive and performance characteristics of 15 kV cables intended for the interconnection of the following equipment in 33/15 kV substations:

- 33/15 kV transformers and 15 kV switchboard,

- 15 kV switchboard and TSA MT/LV transformers,

- 15 kV feeders.

The contractor shall provide the necessary cables, cable ends and accessories for the connection and complete implementation.

###### Key features

- Rated voltage : 11/15 (17) kV

- Cable Type : Single Core

- Conductor : Aluminum (IEC 60228 compliant)

- Insulation : PR (Cross-linked Polyethylene)

- Outer Sheath : PE (Polyethylene)

###### Fire behaviour :

  - Reduced smoke emission (IEC 61034)

  - Halogen-free (IEC 60754-1)

  - Low toxicity and corrosion (IEC 60754-2)

  - Non-flame propagator (IEC 60332-1)

  - Non-propagative of fire (IEC 60332-3)

- Anti-rodent treatment of the outer sheath

- UV resistance (direct sun exposure)

- Waterproofing suitable for prolonged immersion (installation in gutters)

- Conductor cross-section : to be selected according to IEC standard values, justified by design note (ampacity current, short circuit, voltage drop) and taking into account installation conditions and correction factors (IEC 60502-2, Annex B)

###### Reference standards

Cables and accessories must meet the following standards (non-exhaustive list):

- IEC 60502-2 : 6 to 30 kV extruded insulated power cables

- IEC 60502-4 : 6 to 30 kV cable accessories

- IEC 60060 : High Voltage Test Techniques

- IEC 60183 : Guide to choosing high-voltage cables

- IEC 60228 : Insulated Cable Conductors

- IEC 60229 : Testing of Extruded Outer Ducts

- IEC 60230 : Shock tests of cables and accessories

- IEC 60287 : Ampacity Current Calculation

- IEC 60331 : Integrity of Circuits Subject to Fire

- IEC 60332-1 & 3 : Non-Spread of Flame and Fire

- IEC 60754-1 & 2 : Gases emitted during combustion

- IEC 60684 : Flexible Insulating Sleeving

- IEC 60811 : Test Methods for Non-Metallic Materials

- IEC 60885 : Electrical Testing

- IEC 60949 : Calculation of short-circuit ampacity currents

- IEC 60986 : Short Circuit Temperature Limits

- IEC 61034 : Flue Fuel Density

- IEC 61442 : Testing of Cable Accessories

###### Construction requirements

  - Constitution

    - Single-core cable with aluminum core.

    - PR insulation.

    - PE outer sheath, black, anti-UV, anti-rodent treated.

    - Metal screen made of copper or aluminum wire or tape according to IEC 60502-2.

    - Longitudinal and radial waterproofing suitable for installation in channels that can be submerged.

###### Section selection

    - IEC standard sections.

    - Justification by calculation note (permanent current, short circuit, voltage drop).

    - Consideration of installation conditions and correction factors (see IEC 60502-2, B Annex).

###### Fire behaviour

    - Halogen-free, reduced smoke emission, low toxicity and corrosion.

    - Complies with IEC 61034, IEC 60754-1/2, IEC 60332-1, IEC 60332-3.

###### Physico-chemical characteristics

    - UV resistance.

    - Anti-rodent treatment.

    - No exposure to any particular chemical hazards.

###### Sealing

    - Design for extended immersion.

###### Marking

    - Marking on the outer sheath in accordance with IEC.

    - Metric marking recommended.

###### Accessories and Ends

    - Environmentally friendly ends (indoor/outdoor), creepage ≥ 31 mm/kV.

    - Electrochemical torques avoided (use of bimetal plates if necessary).

    - Supply of all accessories necessary for the grounding of metal screens.

###### Junctions

    - No cable junctions are allowed between transformers and MV switchboard.

###### Searching

    - Marking at each end by rings or half-shells made of non-combustible/rot-proof plastic, ivory colour, black marking (phase number, identification of the ends).

###### Grounding of screens

    - Screens connected to the ground at one end only.

    - At the other end, screen socket out and isolated.

    - For cables connected to the HVA grid of the transformer, grounding via the ground protection CT grid.

###### Connections and fittings

    - Accessories for 17 kV, sized for maximum intensities.

    - Use of bi-metal fittings if necessary.

###### Factory testing

  - Reception

    - Presence of the Project Owner and the Consulting Engineer during acceptance.

###### Individual series tests

    - All individual tests provided for by IEC 60502-2 performed on each drum.

###### Sample Testing

    - Sample tests according to IEC 60502-2.

###### Type Testing

    - No type testing required, but providing the type test reports on identical equipment.

###### Documentation to be provided

- Detailed data sheets of cables and accessories.

- Section calculation notes.

- Installation and installation procedures.

- Procedures for grounding screens.

- Factory test report.

- Certificates of conformity to IEC standards.

###### Summary of key requirements

| Characteristics | Key requirements |
| --- | --- |
| Assigned Voltage | 11/15(17) kV |
| Driver | Aluminium |
| Insulation | PR |
| Outer sheath | PE, black, anti-UV, rodent |
| Fire behaviour | LSZH, non-propagator, IEC |
| Section | Based on calculation, IEC value |
| Marking | On duct, metric recommended |
| Searching | Non-combustible rings/tags |
| Accessories | Suitable ends, grounding |
| Junctions | Forbidden between transformer and switchboard |
| Factory tests | IEC 60502-2, PV supplied |

Answers to "technical" clarification questions

AOI N° 06 / CMI/ 2025 for the design, supply and execution of the construction works of the SUD 33/15 kV and NORD 33/15 kV substations, as well as the rehabilitation of six existing substations in the city of Nouakchott in a single lot.

## Technical specification of insulating columns and insulators for the 33/15 kV substations in Nouakchott

#### Object

This specification defines the technical requirements for insulating columns and insulators to be installed in the 33 kV and 15 kV substations in Nouakchott. It aims to guarantee the safety, reliability and durability of equipment in an environment subject to a severe level of pollution.

#### Normative references

All equipment supplied must comply with the latest editions of the following IEC standards:

- IEC 60815: Guide to the selection of insulators under pollution;

- IEC 60273: Characteristics of exterior and interior insulators;

- IEC 61109: Composite insulators for AC overhead lines with a voltage rating greater than 1000 V;

- IEC 60168: Testing of ceramic or glass insulators;

- IEC 62217: Common tests for composite insulators;

- IEC 60120 and IEC 60372: Requirements and tests for insulator chains;

- EN 60305: Glass or porcelain insulators for alternating current overhead lines.

#### Environmental conditions

Pollution level:

- Severe pollution class according to IEC 60815 (presence of sand and salt air).

Climatic conditions:

- The equipment must be adapted to the temperatures, sunshine, humidity and winds of the Nouakchott region.

#### Technical requirements

  - Insulating columns (insulators, supporters)

    - Long shaft type, with external metal frames.

    - Sufficient mechanical strength to withstand the forces due to permanent currents, short circuits and external stresses (wind, traction, etc.).

    - Mounting on galvanized steel brackets.

    - Resistance to thermal shock and UV.

#### Isolator Chains

Answers to "technical" clarification questions

AOI N° 06 / CMI/ 2025 for the design, supply and execution of the construction works of the SUD 33/15 kV and NORD 33/15 kV substations, as well as the rehabilitation of six existing substations in the city of Nouakchott in a single lot.

    - Type tempered glass hood and stem.

    - Minimum mechanical breaking load: 160 kN.

    - Minimum creepage line: 31 mm/kV phase-to-phase voltage, to be adjusted according to the pollution class defined by IEC 60815.

    - The shape of the plates must be adapted to limit the accumulation of pollution and facilitate natural cleaning.

    - The number and type of insulators in each chain will be determined to ensure the required mechanical strength and creepage line.

#### Compatibility

Insulators and insulating columns must be mechanically and electrically compatible with the substation equipment (disconnectors, busbars, etc.).

#### Testing and Compliance

- Mandatory provision of certificates of type and routine tests carried out by an accredited laboratory, attesting to compliance with the applicable IEC standards.

- Testing should include, at a minimum:

- Electrical tests (resistance to operating voltage, resistance to lightning);

- Mechanical tests (tensile, flexural, torsion);

- Pollution resistance tests according to IEC 60815 and IEC 60168;

- Specific tests for composite insulators according to IEC 62217 and IEC 61109.

#### Marking and documentation

- Each insulator/insulating column must bear an indelible marking indicating the manufacturer, the year of manufacture, the type, the pollution class and the main characteristics.

- Provision of a maintenance, installation and storage manual with each delivery.

- Traceability guaranteed by the supplier.

#### Delivery and reception

- The equipment must be delivered with all the necessary accessories for assembly.

- On-site acceptance will be conditional on documentary compliance, the integrity of the equipment and the successful completion of any tests in the presence of the project owner.

#### Additional provisions

- The manufacturer shall verify and justify the conformity of the equipment with the requirements of this specification, in particular with regard to creepage and mechanical strength.

- Any derogation or alternative proposal must be submitted to the project owner for written approval.

Answers to "technical" clarification questions

AOI N° 06 / CMI/ 2025 for the design, supply and execution of the construction works of the SUD 33/15 kV and NORD 33/15 kV substations, as well as the rehabilitation of six existing substations in the city of Nouakchott in a single lot.

# 15 KV AND 33 KV SURGE ARRESTER SPECIFICATIONS

- PURPOSE OF THIS SPECIFICATION

This specification defines the technical characteristics of the 15 kV and 33 kV surge arresters that will be installed in the 33/15 kV substations in Nouakchott.

# CONSISTENCY AND LIMITATION OF SUPPLY

#### Supply

The Contractor undertakes to deliver surge arresters complete and in working order. Its supply includes in particular:

    - Surge arresters

    - The support frame of the surge arresters;

    - A discharge meter;

#### Assembly

The on-site assembly and operation control of the devices include:

    - Mounting surge arresters on their frames

    - Cable connection

    - The execution of the tests in the presence of the Project Manager or his representative,

# KEY FEATURES

In addition to the characteristics common to 15 and 33 kV equipment, HV surge arresters have the following characteristics:

|  | Grid voltage | 15 kV | 33 kV |
| --- | --- | --- | --- |
| • | Type of surge arresters | ZnO without spark gap | ZnO without spark gap |
| • | Maximum Mains Voltage Um | 17.5 kVrms | 36 kVrms |
| • | Maximum voltage in DC service | 15 kEnvms | 33 kVrms |
| • | Rated voltage (your) | 17 kEnvms | 34 kVrms |
| • | Peak Discharge Current Rating | 10kA | 10 kA |
| • | Line Discharge Class | 3 | 3 |

It will be up to the Contractor to confirm these characteristics by all the necessary studies: in particular, the Contractor is requested to carry out a coordination study of isolation and simulation of transient phenomena (lightning surge studies), in order to specify the definition of the surge arrester set, their number and their precise location.

The Contractor shall ensure that the detailed list of required characteristics is provided in the Annex.

The study for the selection of the surge arresters will be submitted to the project owner for approval.

# REFERENCE STANDARDS

In addition to the common standards for 15 and 33 kV equipment, the following specific standards apply:

- IEC 60099 Surge arresters

- Part 4 Metal oxide surge arresters without spark gaps for alternating current networks;

- Part 5 Recommendations for Selection and Use.

# CONSTRUCTION REQUIREMENTS

Each surge protector must include:

The active part containing the zinc oxide pellets:

- A polymer insulating envelope;

- An insulating base;

- A Corona ring (if needed);

- A discharge meter with indication of the leakage current value;

- An insulated cable between the surge arrester and the discharge meter.

The surge arresters must comply with the construction requirements of IEC 60099.

# FACTORY TESTING

A factory acceptance in the presence of the Project Owner and the Consulting Engineer must be carried out.

#### Individual series tests

All the individual series tests specified in IEC 60099-4 must be carried out on each surge arrester.

#### Type Testing

No type testing is required.

A copy of the type test reports carried out on identical equipment shall be provided.

## Technical Specification Lightning Protection & Grounding

33/15 kV substations Nouakchott

##### OBJECT

Define the technical and normative requirements for lightning protection and grounding of metal masses in 33/15 kV substations in Nouakchott, in order to ensure the safety of people, equipment and the sustainability of installations.

##### APPLICABLE STANDARDS

- IEC 62305 : Lightning protection (design, installation, separation of earth circuits)

- IEEE 80 : Safety and design of HV/MV grounding networks (thermal criteria, contact voltages/pitches)

- IEC 60364 : Low-voltage electrical installations

- IEC 61936 : Design and implementation of electrical installations in HV/MV substations

##### LIGHTNING PROTECTION

###### Lightning rods

    - Install lightning rods on the technical building and in the transformer area, covering the entire substation.

    - Each lightning rod must have a dedicated earth downspout, isolated from the metal structures.

    - The grounding of lightning rods must be separated from the general ground circuit of the substation to prevent the propagation of the lightning shock wave to sensitive equipment.

    - The equipment must be sized and positioned in accordance with a lightning protection calculation note (IEC 62305), to be provided by the contractor.

###### Surge arresters

    - Install suitable surge arresters on HV/MV inlets and on sensitive equipment, with specific ground connection.

    - Transformer neutral points and surge arresters must be equipped with ground stakes/electrodes of minimum length 3 m if necessary to meet safety criteria.

##### GROUNDING

###### Outdoor area

    - All metal masses (excluding live bare conductors) must be connected to an underground earth network, meshed, without antennas, at a depth of 80 to 100 cm.

    - The following are concerned: HV equipment, earth disconnectors, frameworks, gantries, electrical cabinets and boxes, neutral points of transformers, CT/TT, cable screens, cable trays, luminaires/masts, transformer rails, fences/barriers, gratings.

    - Earth conductor: bare copper, thermally justified cross-section according to IEEE 80.

    - Connections between conductors: suitable fittings, buried connections prohibited.

    - Fixing the earth cables: with bronze earth shoes, never with plastic clamps.

    - Double connecting shoes for flying earthing distributed as follows:

      - 2 33 kV side of the transformer

      - 2 on the HVA grid (15 kV side transformer)

      - 2 in the 33 and 15 kV HVA train room

    - The finned shoes for MALT works must be accessible on each steel frame (2 per frame in the transformer area).

    - The gratings will be visibly connected to the mechanical controls.

    - Connection to the foot of the beds by bronze earth clogs.

    - The overhead conductors connected by loop to the shoes.

    - The power and control cable screens are grounded at both ends.

    - In the event of demolition of the structure, the integrity of the earth circuit must be maintained (shunt prior to any opening).

###### Design criteria

    - Conductor cross-section and earth network mesh to be justified by calculation note:

      - Thermal criterion for buried conductor and downspouts

      - Touch voltage and step voltage criteria

    - Calculations to be integrated:

      - Soil resistivity (on-site measurements)

      - Maximum phase-to-ground short-circuit current

      - Gravel coating

    - If criteria are not met with the mesh, provide ground stakes/electrodes (≥3 m) at the neutral points of transformers and surge arresters.

    - Total resistance of the earth circuit to be measured and guaranteed < 1 Ohm in dry conditions.

###### In buildings

    - Provide an exposed earth network in all buildings, connected to the earth network at the bottom of the excavations.

    - All metal masses and electrical equipment in buildings must be connected to this earth collector network.

    - Design in accordance with local regulations or, failing that, IEC 60364 and IEC 61936.

##### PRODUCTION AND DOCUMENTATION REQUIREMENTS

- Provide a complete design note justifying lightning protection and grounding (schematics, sizing, measured resistance).

- Provide the installation plans for lightning rods, surge arresters and the earth network.

- Provide ground resistance measurement PVs.

- All connections and equipment must be identified according to the substation's nomenclature and electrical diagrams.

- The work must guarantee the safety of people and compliance with international standards.

##### CHECKS AND TESTS

- Measurement of the earth resistance on site (value < 1 Ohm to be guaranteed).

- Verification of the continuity of all earth circuits.

- Visual inspection of connections, fastenings and accessibility of the earth shoes.

- Functional tests of lightning protection devices.

###### Remark	:

Any modification or extension of the earth network must be preceded by a study and an update of the calculations and diagrams.

The entire system must be designed to ensure life safety, equipment protection, and regulatory compliance.

## Technical specification

400/220 V Power Switchover Table (LVBT)

##### OBJECT

Define the technical, functional and normative requirements of the General Low Voltage Panel (LVBT) ensuring the switching and distribution of 400/220 V power supplies to the various subsystems of the 33/15 kV substation, with source management and operational safety.

##### REFERENCE STANDARDS

  - IEC 61439: Low-voltage switchgear assemblies

  - IEC 60947: Low-voltage switchgear

  - IEC 60085: Electrical insulation

  - IEC 60255: Measurement and protection relays

  - IEC 60269: Low Voltage Fuses

  - IEC 60364 : LV Electrical Installations

  - IEC 60529: Degrees of Protection (IP)

  - IEC 62262: Impact Protection (IK)

  - IEC 61643 : LV Surge Arresters

  - IEC 61869: Instrument Transformers

  - IEC 60502: LV Cables

  - IEC 60332-3, IEC 61034, IEC 60754: Fire behaviour of cables

##### 2. KEY FEATURES

| Characteristics | Value / Requirement |
| --- | --- |
| Assigned Voltage | 400 VAC / 220 VAC |
| Insulation voltage | 1000 V |
| Impact Resistance Voltage | 8 kV |
| Rated current | 400 A |
| Short-term permissible current | 10 kA / 1 s |
| Allowable peak current | 25 kA |
| Neutral Scheme | TN |
| Table Type | Plug-in, form 3b |
| Degree of protection | IP41 (min), IP4X (front) |
| Structure | Compartmentalized columns |
| Fixation | On the ground, LV cables from below |
| Busbar | Copper, optimized cross-section |

| Characteristics | Value / Requirement |
| --- | --- |
| Ventilation holes | Layout without IP degradation |
| Grounding | 2 opposing terminals, collector |
| Lifting Rings | On the top envelope |

- SWAPPING FEATURES

###### Power sources

    - Two 15 kV/400 V auxiliary transformers (ASTs) supply the LVB switchboard.

    - Two sets of bars: "Essential (E)" and "Non-Essential (NE)".

    - Automatic swapping prohibits simultaneous pairing of the two TSA power supplies.

###### Operating Modes

    - HS Swap (Out of Service)

    - TSA 1 priority power supply

    - TSA 2 priority power supply

    - Selection via switch on the front panel

###### Source switching

    - Automatic timed failover in the event of a loss of upstream power, to allow HVA switchover.

    - Transfer conditions: availability of the source, absence of defects on the LVBT.

    - Minimum voltage protection relay (ANSI 27) on each inlet for voltage drop detection.

##### SECURITY AND LOCKS

###### Internal interlocks

    - Prohibition of:

      - Closing of the earth disconnect switch with live busbar

      - Energizing the busbar with closed earth disconnect

      - Extracting a circuit breaker in the closed position

      - Extraction of a circuit breaker in the open position with spring not discharged

    - Mechanical locking of access to live compartments

###### Coupling Lock

    - Prohibition of simultaneous closure of the two inlet circuit breakers (no paralleling of TSAs)

###### External Locks

    - Locks to be provided according to operating instructions and TSA access

##### OPERATING AND SWITCHING COMPONENTS

- Tetrapolar circuit breakers, motorized, chassis pluggable

  - In ≥ 400 A: Air Circuit Breaker (ACB)

  - In < 400 A: Moulded Case Circuit Breaker (MCCB)

- Drawer interchangeability and keying

- Lock system for locking in position

- Electronic trips: overload, short circuit

- Circuit breaker gauge≥ 1.3 x permanent current of protected circuit

##### MEASUREMENT, CONTROL AND SIGNALLING

- Data logger on each inlet (front panel): current, voltage, frequency, power factor, power, energy

- TC and TT provided for measurement and protection

- Voltage presence indicators

- Control-Command Interface:

  - TOR (O/F/S/D) information on terminals

  - Analog measurements (current, voltage) on terminals

  - Communication protocol compatible with the general system of the station

- Synoptic panel on the front panel with position visualization

##### AUXILIARY CIRCUITS

- LV AC and DC distribution

- Terminal blocks for analog signals, TOR, 4-20 mA, with sufficient space and physical separation

- Identical marking to schematics and bills of materials, indelible labels

- Halogen-free, non-fire-spreading, low smoke/corrosiveness, label-free internal wiring

- Wiring running in trunking with removable hood

##### INSTALLATION AND MAINTENANCE

- Access via bolt-on covers or doors (tool or wrench required)

- Thermographic inspection possible on connections

- Removable gland plates at the bottom of the panel

- Easy maintenance, replacement of components without risk of contact under tension

##### TESTING AND DOCUMENTATION

- Individual series tests according to IEC 61439

- Type test report on equivalent equipment to be supplied

- Electrical diagram attached to the inside of the door, protected, printed in indelible ink

- Supply and installation of internal cables, identified

- Comprehensive technical documentation: schematics, bill of materials, design notes, IEC certificates

##### PROTECTIONS

- Proven selectivity between low-voltage protection and downstream equipment

- Ground fault protection (grounding of the neutral BT TSA)

- Surge arresters adapted to the conditions of use

##### BUSBAR

- High-purity copper, current-friendly cross-section and short circuit

- Explicit phase identification

- Solid fixing by dimensioned insulators

##### SPECIAL REQUIREMENTS

- No common point between power circuits, control and signalling

- Electrical continuity between columns maintained even with the covers removed

- Ventilation holes without loss of protection

- Lifting rings on the top casing

###### Remark	:

The Contractor must provide all studies, design notes, diagrams and technical documentation justifying the compliance of the LVB and the switching system with the specifications and regulations in force.

Technical specifications – Lighting and sockets 33/15 kV substations – Nouakchott

##### OBJECT

This specification defines the technical requirements for lighting (indoor and outdoor) and sockets to be installed in 33/15 kV substations (new and rehabilitated), in order to ensure safety, operating comfort and compliance with current standards.

##### REFERENCE STANDARDS

- Lighting : IEC 60598-1, 60598-2-1, 60598-2-3, 60598-2-22, 62722-2-1, 62471,

60529, 60364-7-718, 60068, 61439-1.

- Plugs : IEC 60309-1, 60309-2, 60884-1, 60364 (relevant parts).

- Protection : IEC 60529 (IP), IEC 60068 (climatic conditions).

- All equipment must comply with or be equivalent to these standards.

##### LIGHTING

###### Outdoor lighting

    - Technology : LED luminaires, 230 Vac non-backup power supply.

    - Commands :	On/off	Manual	or	automatic	(photocell/twilight switch).

###### Installation :

      - Fastening to technical buildings, metal frames or tubular masts (3 m high if necessary).

      - Strict compliance with safety distances/isolation.

    - Maintenance : Lamp replacement possible without interrupting the installations.

    - Protection : Tropicalized material, IP65 junction boxes, resistance to dust, humidity, UV.

###### Lighting levels to be guaranteed :

| Zone | Minimum level (lux) | Technical notes |
| --- | --- | --- |
| Perimeter up to 5 m from buildings | 10 | Min. illuminance at a point ≥ 1/4 of the mean and ≥ 1/8 of the point max |
| Car parks, surroundings, slopes | 30 |  |
| Substation enclosure, transformer surroundings | 150 | Outdoor LED Floodlights, Mast or Frame Mounting, IP66 Minimum, IK08 |

    - Recommended type : LED floodlight 100-200 W, 4000-5000 K, IP66 min., aluminium housing.

###### Interior lighting (technical buildings)

    - Technology : LED recessed or surface-mounted luminaires, IP40 min., opal diffuser, UGR<19.

    - Emergency lighting : Autonomous blocks (BAES), 1 hour autonomy, installation in accordance with local standards.

    - Protection : IP65 explosion-proof for battery rooms, dust resistance.

    - Installation : Designed to prevent dust/insect build-up in fixtures.

Lighting levels to be guaranteed :

| Area / Location | Minimum level (lux) | Recommended luminaire type |
| --- | --- | --- |
| Corridors, stairs, access | 75 | LED panel 30-40 W, 60x60 cm, 4000-5000 K, UGR<19, IP40 min. |
| Proximity to cabinets, paintings | 150 | Ditto |
| Battery rooms | 150 | Explosion-proof LED luminaire, IP65 |
| Ancillary/technical rooms | 200 | Ditto |
| Offices, lobby | 300 | LED panel 30-40 W, UGR<19, IP40 min. |
| Control room | 500 | LED panel 30-40 W, UGR<19, IP40 min. |

##### POWER OUTLETS

###### Outside

    - Type : Waterproof industrial plugs with built-in protection, IP66/IP67.

    - Layout : Positioned to cover the maximum area (radius of action ~30 m).

    - Mandatory : 1 socket near each transformer for dielectric oil treatment.

###### Features :

| Type | Voltage/Current | IP rating | Norm | Protection |
| --- | --- | --- | --- | --- |
| 3P+N+T | 400 VAC, 32A | IP67 | IEC 60309-2 | Differential + circuit breaker. |
| 2P+T | 230 VAC, 16A | IP66 | IEC 60309-2 |  |

  - Inside

    - Type : 2P+T 16A, 230 Vac, IP20 min. wall sockets (desks, control room, etc.)

    - Technical rooms : 3P+N+T 16/32A sockets, 400 VAC, IP44.

    - Number : Sufficient to power computer equipment and operating equipment.

    - Feeding :	Taken	Computer	Fed	by	UPS	(power supply	without interruption).

##### HARDWARE RECOMMENDATIONS

- Indoor luminaires : LED recessed/surface, IP40 min., UGR<19, 4000-5000 K, high energy efficiency, low maintenance.

- Outdoor luminaires : LED spotlights, IP66 min., IK08, aluminium housing, 4000- 5000 K.

- Hazardous premises : Explosion-proof LED luminaires, IP65.

- Indoor sockets : 2P+T 16A, 230 Vac, IP20 min.; 3P+N+T 16/32A, 400 Vac, IP44.

- Outdoor sockets : 3P+N+T, 32A, 400 Vac, IP67; 2P+T, 16A, 230 Vac, IP66.

##### DOCUMENTATION TO BE PROVIDED BY THE CONTRACTOR

- Supporting calculation notes for light levels.

- Technical data sheets for luminaires and sockets.

- Layout diagrams.

- Certificates of conformity to IEC standards.

- Installation and maintenance procedures.

- Test and acceptance reports.

##### INSTALLATION REQUIREMENTS

- Respect for bending radii, safety distances and installation methods.

- Easy accessibility for maintenance.

- Protection against crushing, rodents, UV, humidity.

- All circuits protected by adapted RCDs.

###### Note :

The lighting levels indicated are minimum values to be guaranteed, while ensuring good uniformity and visual comfort for the operation and safety of the installations.

## LV Cable Specification and Accessories – 33/15 kV Substations

### OBJECT

Define the technical requirements for low-voltage cables (power, control, instrumentation) and their cabling in the 33/15 kV substations of Nouakchott.

### CABLE CHARACTERISTICS

#### LV Power Cables

    - Rated Voltage : 600/1000 (1200) V

    - Conductor : Copper (IEC 60228)

    - Cross-section : ≥ 1.5 mm² (≥ 6 mm² for current measurement circuits), justified by design note

    - Insulation : Cross-linked polyethylene (PR)

    - Armor/shielding : Continuous copper sheath (corrugated for bending), metal armor mandatory in exposed areas

    - Outer sheath : Polyethylene (PE), black, rodent-proof, UV-resistant if exposed to sunlight

#### Fire behaviour :

      - Reduced smoke emission (IEC 61034)

      - Halogen-free (IEC 60754-1/2)

      - Low toxicity/corrosion (IEC 60754-2)

      - Non-flame/fire propagator (IEC 60332-1, 60332-3-24)

    - Waterproofing : Suitable for prolonged immersion in gutters

#### LV Control and Instrumentation Cables

    - Rated voltage : 500/750 V

    - Conductor : Copper (IEC 60228)

#### Section :

      - Min. 4 mm² for polarity, control, measurement

      - 6 or 10 mm² for current/voltage/auxiliary circuits

      - 1.5 mm² for signalling

      - 2.5 mm² for common circuits (internal wiring)

    - Insulation : PR (cross-linked polyethylene)

    - Outer sheath : PE, black, rodent-proof, UV-resistant if necessary

    - Shielding : Continuous copper shielding against electromagnetic interference

    - Fire behaviour, waterproofing, marking : Same for power cables

#### Internal wiring to equipment

    - Type : Flexible copper conductor (class 5), black thermoplastic insulation (type H07V-H), PVC insulation

    - Operating voltage : 500 V

    - Dielectric Test Voltage : 2000 V

#### Sections :

      - 4 mm² (measurement/order)

      - 2.5 mm² (common)

      - 1.5 mm² (signage)

    - Length : Sufficient to move connections

### ACCESSORIES & GROUNDING

- Crimped lugs and bits, coloured bits for marking

- Type suitable for the environment (indoor/outdoor)

- Bi-metal plates to avoid copper/aluminum electrochemical couples

- All connection and earthing accessories supplied

- All screens and shields connected to ground circuits

### DRIVER IDENTIFICATION AND WIRING

- Identification by numbering, letters or colouring of the insulation according to the function

- Colored tips on each end

- Alphanumeric system compliant with IEC 60446

- Good resistance to ageing and humidity

- Functional registration at each end, according to the diagrams

### INSTALLATION REQUIREMENTS

- Installation adapted to the environment (exterior/interior)

- Crush protection, rodents, UV, immersion

- Compliance with bending radii and recommended installation methods

- Use of dedicated gutters, hoppers or chutes

- All conductors connected to terminal block (max 2 conductors/terminal on the equipment side, 1 on the cable side)

- Internal equipment connections made on the back of the drawers, with separate connectors

### FACTORY TESTING

- Individual tests on each drum (IEC compliant)

- Sample tests according to the standard

- Type test reports on identical equipment to be supplied

### DOCUMENTATION TO BE PROVIDED

- Detailed data sheets for cables and accessories

- Section calculation notes

- Installation and installation procedures

- Factory test report

- IEC Certificates of Conformity

- Object

## Technical Specification – Optical Fiber 33/15 kV substations in Nouakchott

This specification defines the technical characteristics and installation requirements of optical fibers intended for the operation of the control-command and protection system of the 33/15 kV substations of Nouakchott.

###### Scope of supply

The Contractor shall supply and install all the necessary fibre optic cables, including all laying, protection and connection accessories, to ensure the interconnection of the substation equipment.

###### Key technical requirements

| Characteristic | Demand |
| --- | --- |
| Fiber Type | Multimode |
| Material | Silica |
| Wavelength | 1300 nm |
| Diameter | 62.5/125 μm |
| Connection | ST Type Connectors |
| Standards | applicable IEC, including IEC UCA2/61850 for network compatibility |
| Network capacity | 100 Mbits |
| Compatibility | Direct connection to terminal equipment |
| Outer sheath | Rodent repellent for all inter-building connections |
| Mechanical protection | Green protective sheaths for channel connections |

- Installation Requirements

  - Optical fibers must be installed in a protective sheath adapted to the environment (anti-rodent in the inter-building, green in the gutters).

  - Physical connections between equipment and the local network should be as short as possible to limit losses and ensure performance.

  - The fibers must be connectable directly to the substation's terminal equipment.

  - Links between digital protection and programmable logic controllers (PLCs) can be made via a copper Ethernet network if necessary.

###### Standards and compliance

  - All fiber optic cables and accessories must comply with applicable IEC standards.

  - The topology and connectivity of the local network must comply with the IEC UCA2/61850 standard (or recognized international equivalent).

###### Documentation and testing

  - The contractor must provide the technical data sheets of the proposed optical fibres, attesting to compliance with the above requirements.

  - Site plans, wiring diagrams and test procedures must be submitted for validation prior to installation.

  - Continuity, attenuation and quality tests of the link must be carried out after installation and their results submitted to the project owner.

###### Summary of Requirements

  - 62.5/125μm Multimode Fiber, Silica, 1300nm, ST Connectors

  - 100 Mbit network capacity

  - Anti-rodent sheath for inter-building, green sheath for gutters

  - IEC and UCA2/61850 compliant

  - Direct connection to terminal equipment

  - Technical documentation and mandatory tests

.

## Technical Specification of the Gates and Gates of the 33/15 kV substation of Nouakchott

#### Main Portal

  - Type and Dimensions

    - Metal gate with lateral movement on guided wheels.

    - Opening width: 6.00 meters.

    - Height: Same as the fence surrounding the substation.

    - Actuation: Manual.

#### Construction

    - Steel tubular structure.

    - The assembly ensures stiffness and rigidity, while guaranteeing the lightness of the whole.

    - Finishing: hot-dip galvanizing according to current standards.

    - Reinforced frame to ensure stability and mechanical strength.

#### Security

    - Compliance with the NF P 25-362  standard (Closing for free bays and gates – Technical specifications – Safety rules).

    - Railing or filling according to the safety requirements of the site.

    - Possibility of adding barbed wire on the upper part, installed in a similar way to the fence.

#### Accessories

    - Robust guide system on castors, suitable for frequent use.

    - Gate stop in open and closed position.

    - Predisposition for future automation, in accordance with the current regulations on gate automation.

#### Grounding

    - All enclosures, housings and metal masses of electrical equipment installed on or near the gate must be connected to the gate ground.

#### Pedestrian access gate

  - Type and Dimensions

    - Metal gate with a single leaf.

    - Opening width: 1.20 metres.

###### Height: Same as the gate and fence.

    - Manual opening.

#### Construction

    - Steel tubular structure.

    - Frame ensuring stiffness and rigidity with limited weight.

    - Finish: hot-dip galvanizing.

#### Security

    - Compliance with the NF P 25-362 standard.

    - Equipped with  security lock.

    - Supply and installation of the  necessary posts and hinges.

    - Possibility of adding barbed wire on the upper part, installed in a similar way to the fence.

#### Grounding

    - All associated metal masses must be connected to the ground of the gate.

#### Standards and References

Gates, wicket gates and fences must meet the following standards:

- NF P 25-362 : Closing for free bays and gates – Technical specifications – Safety rules.

- NF P 25-363 : Closing for free bays and gates – Safety components – Test methods.

- NF EN 10223 (series): Steel wire and drawn products for fences.

#### Additional requirements

- All metal elements must be protected against corrosion (hot-dip galvanizing).

- Locking systems must be robust and suitable for intensive use in industrial environments.

- Security devices must prevent any break-ins or unauthorized access.

- The installation must be carried out in accordance with the rules of the trade and the requirements of the standards cited.

#### Remark:

The exact dimensions and design details (tube cross-section, lock type, etc.) will need to be specified during the execution phase, depending on the constraints of the site and the client's requirements.