| CHEMTEX |  | SPEC. NO. : IP009-43-03-01 |  | REV. P |
| --- | --- | --- | --- | --- |
|  |  | PROJECT NO : IP009 |  | SH. 1 OF 19 |
| AREA: | ###### ELECTRICAL | DESCRIPTION : | 6.6kV SWITCHBOARD |  |

IP009

PASHMINA PROJECT

SPECIFICATION FOR

6.6kV SWITCHBOARD

MOMENTIVE PERFORMANCE MATERIALS

CHENNAI

CONTENTS

- IDENTIFICATION

- SCOPE

- CODES AND STANDARDS

- SYSTEM PARTICULARS

- SITE ENVIRONMENTAL CONDITIONS

- CONSTRUCTION

- ELECTRICAL DESIGN REQUIREMENT

- ELECTRICAL EQUIPMENT

- MAKE OF COMPONENTS

- EQUIPMENT NAME PLATE

- PAINTING

- INSPECTION & TESTING

- PACKING

- SPECIAL TOOLS

- SPARES

- DEVIATIONS

- QUALITY ASSURNACE

- GUARANTEE

- LIST OF DOCUMENTS ATTACHED

- VENDOR DRAWINGS & DOCUMENT REQUIREMENT SCHEDULE

- TECHNICAL PARTICULARS

1.0	identification :

REV

| ##### ITEM NO | QTY | DESCRIPTION |
| --- | --- | --- |
| 1545-E01 | 01 | MV SWITCHBOARD |

2.0	SCOPE :

This specification covers minimum requirements for the design, manufacture, assembly, testing at manufacturers works, packing and delivery at site of 6.6 kV switchboard with complete accessories. This shall also include erection supervision, testing & commissioning and guarantees for operation of 6.6kv switchboard including minor modifications at site, for trouble free operation of Pashmina project, Orgadam, Sriperambudour taluk, Kancheepuram district, Tamil Nadu, approximate 50 kms from Chennai.

3.0	CODES & STANDARDS :

Shall comply to latest editions of following relevant codes & standards, safety codes, Regulations of statutory Authorities (Chief Electrical Inspectorate to State Government).

IS : 5		Colour ready mixed paint & enamels

IS : 722	Specification for ac electricity meters

IS : 1248	Specification for direct acting indicating analog electrical measuring instruments & its accessories.

IS : 3427	Metal enclosed switchgear and control gear for voltages above 1000V but not exceeding 11000V.

IS : 5578	Guide for marking of insulated conductors.

IS : 9920	Switches and switch isolators for voltages above 1000V.

IS : 9921	AC Disconnectors and earth switches for voltage above 1000V.

IS : 2705	Specification for current transformers.

IS : 3156	Specification for voltage transformers.

IS : 3231	Specification for electrical relays for power system protection.

IS : 13118	Specification for high voltage alternating circuit breakers.

IS : 13703	Low voltage fuses for voltages not exceeding 1000V AC or 1500V DC.

IS :  5578 /IS 11353	marking and arrangement of busbars.

Local statutory regulations,

Indian electricity rules 1956,

Indian electricity act-1910

Applicable codes and standards shall be the latest issue to the date of enquiry including addenda, revisions or supplements.

4.0       SYSTEM PARTICULARS:

Power supply	             :  6.6kV, ± 10%, 50 Hz ± 3 %, 3 phase, 3 wire AC

Three Phase Symmetrical Fault Level      : 31.5 KA for 3Sec.

Grounding of neutral		       : Resistance grounding

Control supply

a) Closing, tripping & indication		       :  110V DC supply

b) Space heater supply 		       :  230V 50 HZ 1PH, 3W AC supply

5.0	SITE ENVIRONMENTAL CONDITIONS:

Atmospheric Temperature		       :	Max ---0 C,  Min ----0 C

Design ambent temperature                     :	450 C

for electrical equipment

Relative Humidity                                      :	88% MAX, 77% MIN

Altitude mean sea level		       :	16 mts

Monthly heaviest rainfall		       :	143 mm

Monthly mean wind speed		       :	10 KMPH

Seismic Intensity			       : 	Zone III

Installation		       :	Pressurized room

6.0	CONSTRUCTION :

6.1	GENERAL REQUIREMENTS :

Switchboard shall be designed & constructed to facilitate inspection, cleaning, repair and maintenance and ensure absolute safety during operation, inspection and maintenance.

Each cable compartments shall have inspection cutout with suitable transparent sheet.

Suitable arrangement to be provided to carry out Thermography of cable compartment.

Terminal strip for outgoing control cables connections should be accessible to facilitate working and testing with breaker in test / service condition and while the switchgear is energized.

The draw out carriage on the switchgear shall have three positions - ‘Service’, ‘Test’ and ‘Draw Out’. Automatic safety shutters shall be provided to ensure the inaccessibility of all live parts after the breaker is drawn out. The outer door shall be padlockable for safety. All circuit breaker trucks of the same rating shall be interchangeable. Suitable interlocks shall be provided to prevent faulty operation.

Incoming & Outgoing circuit breakers shall be intelligent microprocessor based with communication unit for :

- Status, alarm and maintenance information.

- Control commands & configuration settings.

Operator interface shall be provided at each switchboard via Man Machine Interface (MMI). :

a) 	MMI shall display measured values & status information, and shall enable operator to configure, control & monitor all fields connected to communication unit.

b)	Provision for connecting Laptop shall be provided.

c)	MMI shall guide the operator through system configuration with user friendly text and prompts.

d)	MMI shall have LCD display with atleast 6 Line – 21 character with provision for sorting & suitable means for easy navigation through the list of data, parameters, alarms & trips shall be provided.

The equipment, software and the network system must be qualified and tested to assure reliability, and tested to confirm all parts operate independently and as an integrated system.

Intelligent Switchgear communication unit shall connect all breaker & protection relays as required for control & monitoring of each feeders like Status, control, measuring values, Alarms with trip.  The communication ports shall be such that the devices can be plugged or unplugged without network disruption.

The system shall use device level communication network, intelligent motor control components, and integrated pre-configured software.

Programmable parameters for the protective functions like trip level, warning level, time delay, and inhibit window current monitoring, phase, average, percent full load, ground fault, imbalance and thermal capacity used diagnostics, time to overload trip/reset, history of trips shall be possible.

Modbus Module for communication with DCS :-

For communication with DCS, Master slave MOD BUS according to RS232C, RS 422 and RS 485 shall be considered.  Each bus shall carry the following signals to and from DCS and scan time shall be less than or equal to 200 Milliseconds. :

- Floating values for motor current, working hours, Kilowatt,etc.,

- Status bits for motor viz., motor running indication, stop indication and motor tripped on fault.

- Command bits to motor start/stop.

Mod Bus redundant modules shall have the feature of automatic switching over from primary to secondary modbus modules in case of module fail, slave primary fail or data cable disconnected. Switching over shall be self-action without external software or control block.

Selection sizing & suitability of all components shall be the vendor responsibility and all equipments required for safe and satisfactory operation shall be included by the vendor, even if it is not specifically mentioned.

All relays, meters and control components shall be mounted on the panel front only.

6.2	ENCLOSURE :

Enclosure shall be made of cold rolled sheet steel of adequate thickness not less than 2mm, assembled to form a rigid, freestanding, dead front structure. Vertical units shall be assembled to form a continuous line up of uniform height. It shall be possible to extend the switchgear from both sides.

Switchboard shall be totally enclosed dust and vermin proof. If necessary louvered openings with wire mesh shall be provided for natural ventilation.

Neoprene gaskets shall be provided for all covers and openings. Minimum protection class for the enclosure shall be IP- 51.

Each cubicle shall be fully compartmentalized with metallic partitions having separate chambers for Main Bus bars, CT’s and Cable terminations, switching device, LV chamber for metering, protection and control equipment.

Independent pressure release flaps/vents shall be provided for each compartment.

All hardwares shall be corrosion resistant. All joints and connections of panel members shall be made by zinc passivated or cadmium plated high quality steel bolts, nuts & washers secured against loosening.

Suitable eyebolts for lifting of panel shall be provided. On removing the eye bolts no holes offering access to panel shall be permitted. Cable supporting facility shall be provided in cable alley for power and control cables.

6.3	BUSBARS :

Busbars shall be made of electrolytic grade copper “OR” aluminium and shall be sleeved with Tracking Resistant material. Fiber glass/ metal sheet with cast resin bushing partitions shall be provided at every junction between two adjacent cubicles.

Busbar joints shall be provided with high tensile bots with spring washers. Prior to joining, oxide-inhibiting grease shall be applied after cleaning the surfaces. Joints shall be taped and shrouded.

Busbars shall extend through all units of the switchgear line up. Busbar cross –section shall be selected based on the temperature rise indicated. Main busbar shall be of uniform cross-section and shall be sized to carry continuously the current specified in SLD. Feeder busbar shall be rated corresponding to breaker rating. Ground busbar shall run throughout the length of the switchgear. Busbars shall be provided with suitable color marking for phase identification.

Busbars shall be housed in a separate chamber. Wire guards / mesh shall be provided inside the sheeting to allow visual inspection of busbars / CT / PT / cable termination and to avoid accidental touch when rear cover is removed.

Busbars shall be supported at regular intervals and both busbars and the supports shall be adequately sized and braced to withstand the specified short circuit level without permanent deformation. All bus supports shall be of non- hygroscopic, flame retardant insulating supports.

6.4	GROUNDING:

All doors and movable parts shall be connected to ground bus with flexible copper connections. Provision shall be made to connect the grounding busbar to the plant grounding grid at two ends. All non-current carrying metallic parts of the equipment shall be grounded.

6.5	ARRANGEMENT OF INTERNAL WIRING AND TERMINATIONS :

The internal wiring for control, signaling, protection and instrument circuits shall be done with PVC insulated conductors, neatly tie wrapped together enclosed in plastic channels.

Conductors shall be terminated with adequately sized compression type lugs. Not more than one outgoing wire shall be connected per terminal. Terminal strips shall preferably be separated from power circuits by metal barriers or enclosures. All spare contacts of auxiliary relays, timers etc. shall be wired up to the terminals. Minimum 6 nos. spare terminals shall be provided on each terminal block.

Wiring shall be carried out with 1100 Volts grade. Each wire shall be identified at both ends by correctly numbered ferrules.

All internal control wiring shall be carried out by stranded insulated copper wires of 2.5 mm2 for power and current circuits and 1.5 mm2 for potential and all other control circuits.  Color Coding for internal panel wiring shall be as per vendor’s standard.

All inter panel control wiring shall be done by the switchgear vendor. Plugs provided should have scraping ground terminal. All shipping section of the panel shall have proper identification and ferruling for joining shipping section at site.

One AC & one DC control power supply feeder shall be made available by owner. The vendor shall arrange supply to each cubicle with individual isolation

6.6	CABLE ENTRY AND TERMINATIONS:

Incoming & Outgoing power connection shall be through XLPE cables. Suitable termination arrangement shall be provided for number and size of cables as specified in Data sheets.

Cable entry shall be from bottom, ample space for connection of cables shall be provided at the rear of the switchboard. Cable lugs for power and control cable with requisite bushings for sealing power cable entries shall be included in the scope of supply of the switchgear.

The switchgear shall be supplied complete with supports for clamping incoming & outgoing cables. Terminal blocks shall not be used to support cables. The head room available between cable gland plate and terminal lug shall be sufficient so as to allow proper termination of cables.

6.7	SPECIFIC REQUIRMENTS:

CIRCUIT BREAKER COMPARTMENT:

During the truck withdrawal the shutters shall cover the branch bars automatically for circuit breaker connection.

In this compartment also the operation linkage for the earthing switch shall be incorporated in order to guarantee necessary interlock between earthing switch and circuit breaker.

Triple pole earthing switches shall be provided. They shall be installed in the cable compartment.

Circuit Breaker truck:

All the withdrawable elements shall be mounted on a stable sheet steel construction in the same manner, as the cubicle’s front on which circuit breaker is mounted.

The truck shall be provided with three / four, large rollers, which allows it to be readily wheeled on all types of floors.

The arrangement of the contacts shall ensure extreme robustness and stability under fault conditions.

Mechanical interlocking shall be provided to fulfill the following functions:

To prevent the truck from being moved from the test to the service position or vice versa when the circuit breaker is closed.

To prevent the closing of the circuit breaker while the truck is at any intermediate point between the test and locked in service position.

The plug of the secondary wiring will automatically engage when the truck is moved into the service position.

In the reverse operation, the plug remains engaged until withdrawn by hand on the truck and it is removed from the cubicle.

Cable compartment:

This compartment shall be accessible from the rear of the cubicle and designed to. accommodate the following equipment:

- Current Transformers.

- Voltage Transformers

-     	Earthing Switch.

Cable-end Boxes. Cable box shall be suitable for the cable sizes as mentioned in the enclosed SLD.

The normal arrangement of the cubicle shall be for cable entry from below the cable boxes being fitted at floor level.

Low voltage compartment:

In order to accommodate the protection relays, control and indicating equipment a separate compartment in the upper part of the cubicle front shall be provided.

All indicating equipment such as relays, ammeters etc. shall be mounted on the front door.  Auxiliary relays, fuses, CT terminals, MCB’s etc. shall be mounted and wired in the LV compartment.

Auxillary contactors/relays/terminals shall be suitable for mounting on DIN rail.   Separate terminal blocks shall be considered for “Closing signals”, “Tripping signals”, “Auxillary contacts”, “mA signals (if any)” etc.

Control circuits:

The equipment shall be designed in accordance with IEC standard recommendations to operate with an over voltage up to 10 % and under voltage up to 15 % except for the tripping and closing circuits.

The tripping circuit allows an operation with 70 % to 110 % of rated DC auxiliary voltage supply, the closing circuit allows an operation with 85 % to 110 % of rated DC or AC auxiliary voltage supply.

For the protection of the different circuits such as control voltage supply, charging motor, heater etc.  where applicable MCB's shall be provided individually for each cubicle circuit.

For receiving and Distributing AC and DC power for control circuit suitable rated 2 pole MCB’s to be considered.

“MCB off” indicating lamp to be considered in case of MCB (DC) is “OFF”.

- ELECTRICAL DESIGN REQUIREMENT :

7.1	FAULT PROTECTIONS AND INTERLOCKS:

Each circuit breaker cubicle shall be provided with necessary protection relays as per single line diagram. Remote interlock & inter trip facility for all the incoming & outgoing circuit breakers shall be provided.

The incomer panel shall be provided with a load manager (with RS 232 / RS 485 port) having digital electronic meter, which shall monitor atleast the following measurements

- Phase & Line voltages

- Phase currents

- Ground currents

- kVA, kW, kWh

- kVAR, kVARh

- Power factor, frequency and overcurrent and earthfault relays.

Distribution transformer feeders shall be furnished with auxiliary relays for alarm and trip indications. Each transformer feeders shall have provision to receive the following transformer fault alarm & trip signals

- Winding Temperature Alarm

- Winding Temperature Trip

- Buchholz Alarm

- Buchholz Trip

- Oil Temperature Alarm

- Oil Temperature Trip

- Magnetic Oil Gauge Alarm

The above trip & alarm signals shall trip the transformer feeder & provide annunciation. Transformer feeder shall not be tripped in case of bus under voltage.

Intertripping connection between 6.6KV Switchboard incomer breakers & upstream breakers shall be provided.

Static annunciation facility to be provided for each transformer outgoings. Ten window annunciator with hooter shall be provided on each outgoing feeder for transformer fault alarms with provision for testing the annunciator window lamps and hooter. Push buttons for fault acknowledge, reset and lamp test shall be provided. Also four-window annuciator facia with in built push buttons shall be provided for each incomer for under voltage indication.

A common fault annunciation contact for each feeder shall be wired to terminal block to be connected to the DCS.

8.0	ELECTRICAL EQUIPMENT :

8.1	VACUUM CIRCUIT BREAKER :

Circuit Breaker shall be draw out type, trip free and shall have anti-pumping facilities. Breaker current ratings and short circuit ratings shall be as indicated in the Single line diagram. Circuit breakers shall be designed with low switching over voltage level and long switching life.

The breakers shall have motor operated spring charged mechanism. It shall be possible to charge the springs manually, if required. Mechanical indication of spring position - charged/discharged shall be provided. In case the limit switch fails to cut out the spring charging motor when the springs are fully charged the motor shall be automatically de-coupled and annunciation for this shall be provided. Energy storage shall be sufficient for an open-close-open operation at rated capacity.

The breakers shall have 8 NO + 8 NC spare auxiliary contacts. If these are not available an auxiliary contactor shall be used to multiply the auxiliary contacts of the breakers. All auxiliary contacts shall be wired to the terminal block.

Each breaker shall be provided with an operation counter and mechanical ON – OFF indicator.

An integral earth switch system or separate earthing carriage shall be provided. After withdrawing the circuit breaker, this can be inserted to facilitate grounding of cables.

Suitable electrical interlock along with audio / visual indication shall be provided to prevent closing of earthing truck on live busbars.

8.2	INSTRUMENT TRANSFORMERS :

Current transformer, Potential transformer and measuring instruments to be provided by vendor as shown in attached SLD.

Current and voltage transformers shall be cast resin insulated. Primary and secondary terminals shall be marked distinctly.

8.2.1	Current Transformers (CT) :

Current Transformer shall be mounted on the switchgear stationary parts. The CT ratio & burden shall be as shown in the single line diagram.

a)	Accuracy class 1.0 for metering.

b)	Accuracy class 5P 20 etc. for relays.

8.2.2	Potential Transformers (PT) :

The potential transformers shall be drawout type and provided with primary and secondary fuses. Burden and accuracy class shall be in accordance with the load requirements .  Burdens shall be selected to suit relay / Instrument loads selected by Vendor.

The drawout mechanism shall disconnect the busbars before the PT or its primary fuses become accessible.

8.3	MEASURING INSTRUMENTS :

All measuring and recording instruments shall be digital, flush mounting type.

Digital metering unit shall provided for Incoming and outgoing feeders The digital metering unit shall have provision to display the following:

Phase and Line Voltage

Phase currents

kVA, kW and kWH

Power factor

Frequency

Alarm output relay

All meters shall have provision of RS 235/RS485 connection for monitoring of Power at DCS.

All auxiliary equipment such as shunts, transducers, CT’s and PT’s that are required shall be included in the supply.

8.4	RELAYS:

Relays shall be drawout, microprocessor based flush mounting type fitted with dust tight covers. The relay shall be adjusted over a wide range to provide discrimination with devices having different characteristics. Non-protection relays can be of fixed type. Relays shall have ‘built in’ flags to indicate relay operation. It shall be possible to reset the flag without opening the relay case. The relays shall be suitable for 110 V, DC supply.

Relays shall be RS232, RS422 and RS485 ports for communication with DCS.

8.5	INDICATING LAMPS & PUSH BUTTONS :

Color coding of push buttons & indicating lamps shall be as follows :

|  | PUSH BUTTON |  | INDICATING LAMPS |  |
| --- | --- | --- | --- | --- |
|  | Alarm Reset | Yellow | Running / ON | Green |
|  | Lamp Test | Green | Stop / OFF | Red |
|  | Trip circuit “healthy” check | Black | Fault / Auto trip | Amber |
|  |  |  | Spring Charged | White |
|  |  |  | Control power “healthy” | White |
|  |  |  | D.C. failure | Blue |

Low power consumption indicating lamps/LED shall be used with translucent lamp covers to diffuse light. Lamps shall be supplied complete with the necessary current limiting resistor.

8.6	CONTROL SWITCHES :

Each circuit breaker feeder shall be provided with Trip-Neutral-Close control switch.

All control switches shall be rotary, back connected type having a cam operated contact mechanism. Phosphor bronze contacts shall be used on the control switches. Circuit breaker control switches shall be 3-position spring return to neutral. They shall have ‘Pistol Grip’ handle. Number of ways, locking system, lost motion device, if required etc. shall be shown on the relevant schematic drawings. Two ‘spare’ ways shall be provided on these switches.

8.7	SPACE HEATERS AND ILLUMINATION :

Space heater for each cubicle / vertical panel shall be located at the bottom of the switchgear and shall be controlled through a thermostat with an adjustable setting and a manually operated switch. Provision shall be made for space heater circuit for all motors.

Panels shall have fluorescent light fittings for internal illumination with door switch.

9.0	MAKE OF COMPONENTS

| SL.NO. | ITEM | MAKE |
| --- | --- | --- |
| 1. | Protective Relays | ABB/SIEMENS/Equivalent |
| 2. | Auxiliary Relays | ABB/SIEMENS/GE |
| 3. | Breaker Control Switch | ABB/EASVNROYRALLE/ Equivalent |
| 4. | Selector Switches | SIEMENS/L & T |
| 5. | Digital Meters | ENERCON/AE |
| 6. | Push Buttons & Indication Lamps | SIEMENS/L & T/RAAS CONTROLS |
| 7. | Vacuum Bottles | WESTING HOUSE/TOSHIBA |
| 8. | MCB | MDS/HAVELLS/INDO ASIAN |
| 9. | Control Transformer | INDCOIL/AED/KAPPA/PRECISE |

10.0	EQUIPMENT NAMEPLATES:

Permanent non-corrosive nameplate with white background and black letters shall be fixed on the each compartment indicating item no and service description as shown on the Single Line Diagram. The nameplate shall indicate the following:

First Line		:	Equipment Item No.

Second Line	:	Equipment description

Third Line	:	Equipment description

Master nameplate shall be provided indicating as a minimum the switchgear volt, volt-ampere rating, short circuit rating, item number and manufacture’s name and model number.

Name Plate shall be provided on each equipment (PB’s, Indication Lamps, Auxiliary Relays, Selector Switches etc) those mounted on the Switchboard.

Listing and Labeling : The switchboard and all devices mounted thereon shall be listed and labeled for their intended use.

11.0	PAINTING:

All metal surfaces shall be thoroughly cleaned and degreased to remove mill scale, rust, grease and dirt. Fabricated structures shall be pickled then rinsed to remove any trace of acid. The under surface shall be prepared by applying a coat of Phosphate paint and a coat of yellow Zinc Chromate primer. The under surface shall be free from all imperfections before undertaking the finishing coat.

After preparation of under coat, the Switchboard shall be spray painted with two coats of epoxy based final paint. The color shade of final paint shall be shade 631 (light grey) as per IS : 5. Spray painted finished panels shall be dried in stoving ovens in dust free atmosphere.

12.0	INSPECTION AND TESTING :

- Equipment shall be tested and Inspected at manufacturers works before dispatch to ensure compliance with relevant specifications, drawings, Codes & Standards.

The Owner or his representatives may visit the works during manufacture of various equipment to access progress of work as well as to ascertain the Quality of raw materials used.

Owner shall be given minimum four weeks advance notice for witnessing the final testing. The minimum testing requirements for all components/ equipment shall confirm to the requirements stipulated in applicable codes & standards.

Tests shall be carried out at manufacturer’s works under his care & expense. All routine tests as specified in applicable standard codes shall be conducted:-

- Dimensional checks,

- Continuity checks,

- Component Rigidity checks,

- Insulation resistance checks,

- High Voltage tests Etc.

Type tests certificate for the similar type of Equipment shall be furnished along with the bids. Manufacturer shall submit separate quote for the Type tests.

13.0	PACKING :

The panel shall be shipped to site packed in wooden crates. They shall be wrapped in polyethylene sheets before being placed in crates to prevent damage to the finish. Crates shall have skid bottoms for handling.

- SPECIAL TOOLS:

A set of special tools which are necessary or convenient for erection, commissioning, maintenance and overhauling of the equipment shall be included in the scope of supply.

The tools shall be shipped in separate containers, clearly marked with the name of the equipment for which they are intended.

- 15.0	SPARES:

The vendor shall provide required number of spares for two (2) years of satisfactory and continuous trouble free operation.

Also, required commissioning spares shall be provided by seller free of cost.

16.0 	DEVIATIONS :

Any deviations from the requirements of this specification shall be stated as exceptions in Vendor / contractor’s proposal. Unless specific exceptions are stated, it shall be understood that the equipment is in complete accordance with the specification.

- QUALITY ASSURANCE:

Manufacturer shall follow his standard procedures for Quality Assurance and control. However, the standard procedures shall be submitted to the owner in extent of order.

The procedure shall be in such a form as to clearly delineate the manufacturing sequence and major inspection points and to reference manufacturer’s test and inspection procedures.

The owner will inform the manufacturer as to which of the Inspection points and tests will be witnessed.

18.0 	GUARANTEE :

Guarantee shall be for proper design, installation and workmanship. Vendor / contractor shall guarantee all performance parameters. The guarantee shall be for a period of 12 months from the date of commissioning or 18 months from the date of last supply whichever is earlier.

19.0	LIST OF DOCUMENTS ATTACHED:

Vendor to follow the following drawings as a reference, to make uniformity in engineering design of Motor Schematics and drawings.

|  | SR. NO. | DESCRIPTION | SPEC. NO. / DWG. NO. | NO. OF SHEETS | REV | REMARKS |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1.0 | Symbols for schematics and SLD & schematic wiring diagram symbols | 108001-9999-009 | 3 | P |  |
|  | 2.0 | SLD for 6.6kV Switchboard#1 | 408302-1540-009 | 1 | P |  |

- VENDOR DRAWINGS & DOCUMENT REQUIREMENT SCHEDULE

| FOLLOWING ENGINEERING DATA IS TO BE SUBMITTED BY THE VENDOR WITH OFFER AND AS PART OF PURCHASE ORDER. EQUIPMENT ITEM NO AND ENQUIRY/P O NO. TO BE CLEARLY MARKED ON ALL DRAWINGS / DATA. P/X = PRINT/XEROX S=REPRODUCIBLE SEPIA/ ORIGINAL |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SR |  |  | REQUIRED | REQUIRED AFTER P.O. |  |  |  |  |
| NO. | ENGINEERING DATA |  | WITH OFFER | FOR APPROVAL | CERTIFIED FINAL |  |  | REMARK |
|  |  |  | P/X | P/X | P/X |  | S |  |
| 1 | OVERALL DIMENSIONAL DWG. WITH SPACE REQUIRED FOR OPERATION & MAINTENANCE, CABLE ENTRIES & BUS DUCT. |  | 1 | 3 | 6 |  | 1 |  |
| 2 | MODULE SIZE, DIMENSIONS, MAKE FOR EACH DEVICE. |  | 1 | 3 | 6 |  | 1 |  |
| 3 | FOUNDATION PLAN WITH STATIC & DYNAMIC LOADS INCLUDING FIXING DETAILS |  | 1 | 1 | - |  | 1 |  |
| 4 | ENCLOSURE PROTECTION DETAIL |  | 1 | 3 | 6 |  | 1 |  |
| 5 | CONTROL SCHEMATIC DIAGRAMS & G. A. DRAWING FOR PANEL WITH TERMINAL PLAN. |  | - | 1 | 6 |  | 1 |  |
| 6 | WIRING DIAGRAMS |  | - | - | - |  | - |  |
| 7 | BILL OF MATERIALS |  | 1 | 3 | 6 |  | 1 |  |
| 8 | DESIGN CALCULATIONS FOR BUSBARS SIZING (THERMAL & DYNAMIC) |  | 1 | 3 | 6 |  | - |  |
| 9 | MECHANICAL SEAL DETAILS & DWGS. |  | - | - | - |  | - |  |
| 10 | TEST CERTIFICATES FOR ALL COMPONENTS AS APPLICABLE a) ROUTINE TEST b) TYPE TEST c) PERFORMANCE TEST d) STATUTORY AUTHORITIES IF ANY |  | - | - | 6 |  | - |  |
| 11 | TECHNICAL CATALOGUE & LIST OF USERS |  | 1 | - | 6 |  | - |  |
| 12 | INSTALLATION & OPERATION MANUAL |  | - | 1 | 6 |  | - |  |
| 13 | MAKE TYPE & CATALOGUE NO. & RATING OF EACH COMPONENT WITH CO-ORDINA- TION BETWEEN OVERLOAD RELAY RANGE & FUSE |  | - | - | 6 |  | 1 |  |
| 14 | DETAILS OF UTILITY REQUIREMENT |  | - | - | - |  | - |  |
| 15 | BASE FRAME DETAILS |  | - | 1 | - |  | 1 |  |
| 16 | ADDITIONAL BASE FRAME DETAILS |  | - | - | - |  | - |  |
| 17 | DEVIATIONS IF ANY |  | 1 | - | - |  | - |  |
| 18 | PRICED SPARES LIST FOR 2 YEARS SERVICE |  | 1 | - | - |  | - |  |
| NOTES : 1. FINAL DOCUMENTS TO BE SUBMITED SEPERATELY IN A FOLDER FOR EACH ITEM. |  |  |  |  |  |  |  |  |
|  |  | VENDOR DATA SCHEDULE |  |  |  | FNA 0804 |  |  |
| CHEMTEX |  | FOR 6.6kV SWITCHGEARS |  |  |  | SPEC. NO. IP009-43-03-01 SH NO.1 OF 1 REV. P |  |  |

21.0	TECHNICAL PARTICULARS :

| SL. NO. | DESCRIPTION | PURCHASER’S REQUIREMENT |  | BIDDER TO FILL IN |
| --- | --- | --- | --- | --- |
| A | GENERAL : |  |  |  |
| 1 | Make | ABB / SIEMENS / ALSTOM |  |  |
| 2 | Enclosure | IP51 |  |  |
| 3 | Type | Intelligent |  |  |
| 4 | Overall Dimensions in mm | Vendor to specify |  |  |
| 5 | Thickness of sheet metal | 2mm for load bearing members, doors & gland plates. 3 mm for base frame. |  |  |
| 6 | Cable entry | Bottom. |  |  |
| 7 | Maximum system voltage | 7.2 kV |  |  |
| 8 | Paint shade | Grey( RAL-7032) |  |  |
| 9 | Overall weight of the Panel (kg) | Vendor to specify |  |  |
| 10 | Communication unit | Required |  |  |
| 11 | Man machine Interface (MMI) | Required |  |  |
| 12 | Feeder presets functions for Alarm levels, Trip levels & Trip delays | Required |  |  |
| 13 | Configurable protection functions | Required |  |  |
| 14 | Display of Status Reporting & supervision functions at MMI | Required |  |  |
| 15 | Serial link communication to DCS system. | Required |  |  |
| B | BUSBAR |  |  |  |
| 1 | Busbar Material | Electrolytic Copper |  |  |
| 2 | Busbar insulation | Flame retardant cast resin material |  |  |
| 3 | Busbar supports | Flame retardant track-resistant polyester glass or porcelain |  |  |
| 4 | Continuous current rating | As specified in SLD |  |  |
| 5 | Short circuit withstand current | 31.5 KA for 3 Sec. |  |  |
| 6 | Maximum temperature rise over ambient temperature of 45°C | 70°C |  |  |
| 7 | Ground Bus : Material / Size | Copper |  |  |
| 8 | Grounding conductor : Material / Size | Copper / 70mm2 |  |  |
| C | CIRCUIT BREAKER | Vacuum |  |  |
| 1 | Type |  |  |  |
| 2 | Maximum system voltage / nominal system voltage | 7.2KV / 6.6 KV |  |  |
| 3 | Rated continuous current at design ambient temperature |  |  |  |
|  | i) Incoming & Tie-breaker CBs | As per Single Line diagram |  |  |
|  | ii) Outgoing circuit breakers | As per Single Line Diagram |  |  |
| 4 | Short time current withstand for 3 sec | 31.5KA |  |  |
| 5 | Rated short circuit making current | 80KA |  |  |
| 6 | Operating duty | O - 0.3 sec – CO - 3 sec - CO |  |  |
| 7 | Total break time | Less than 5 cycles |  |  |
| 8 | Withstand test voltage |  |  |  |
| 9 | i) One minute power frequency | 20 kV |  |  |
|  | ii) Impulse withstand voltage | 60 kV |  |  |
|  | Operating mechanism | Electrical with antipumping feature |  |  |
| 10 | Provision for manual spring charging | Yes |  |  |
| 11 | No. of auxillary contacts | 15 |  |  |
| D | CURRENT TRANSFORMER : |  |  |  |
|  | Make | Reputed |  |  |
| 1 | Type / Class of insulation | Cast Resin,Bar primary |  |  |
| 2 | Ratio, accuracy and burden | As per single line diagram |  |  |
| 3 | Class | 5P20 for protection 1.0 for metering |  |  |
| E | POTENTIAL TRANSFORMER |  |  |  |
| 1 | Make | Reputed |  |  |
| 2 | Type / Insulation Class | Cast Resin / Bar primary |  |  |
| 3 | Rated voltage : Primary / Secondary | As per single line diagram |  |  |
| 4 | Accuracy class/ Rated Burden | As per single line diagram |  |  |
| F | RELAYS / METERS | As per single line diagram |  |  |
| 1 2 3 | Make | SIEMENS/ABB/ L & T/GE |  |  |
|  | Type | Numerical type 110V DC Make : Areva/ ABB / SIEMENS |  |  |
|  | Control voltage | 110V DC |  |  |
| G | EARTHING TRUCK | Built in off load earthing switch for each breaker and separate bus earthing switch with (Electro mechanical) interlock OR Earthing trucks for bus earthing and cable earthing with safety interlocks and visual indication |  |  |
| H | HEAT LOAD |  |  |  |
| 1 | Heated load per panel (KW) | Vendor to specify |  |  |
| 2 | Total heat load (KW) | Vendor to specify |  |  |
| J | AUXILIARY SUPPLY |  |  |  |
| 1 | Space heater / Cubicle lamp | 230 Volts, 1 Phase, 50 Hz |  |  |
| 2 | Utility duplex receptacle | 230 Volts, 1 Phase, 50 Hz |  |  |
| 3 | Closing / tripping coil/ Indication | 110V DC |  |  |
| K | OTHERS |  |  |  |
| 1 | Commissioning spares and tools | Vendor to specify |  |  |
| 2 | Spare parts for 2 years | Vendor to specify |  |  |