| CHEMTEX |  | SPEC. NO. : IP007-43-03-02 |  | REV. 0 |
| --- | --- | --- | --- | --- |
|  |  | PROJECT NO : IP-007 |  | SH. 1 OF 17 |
| AREA: | ###### ELECTRICAL | DESCRIPTION : | M.V. SWITCH BOARD |  |

IP-007

PASHMINA PROJECT

SPECIFICATION FOR

M.V. SWITCH BOARD

MOMENTIVE PERFORMANCE MATERIALS

CHENNAI

CONTENTS

- IDENTIFICATION

- SCOPE

- CODES AND STANDARDS

- SYSTEM PARTICULARS

- SITE ENVIRONMENTAL CONDITIONS

- CONSTRUCTION

- ELECTRICAL EQUIPMENT

- MAKE OF COMPONENTS

- EQUIPMENT NAME PLATE

- PAINTING

- INSPECTION & TESTING

- PACKING

- SPECIAL TOOLS

- SPARES

- DEVIATIONS

- QUALITY ASSURNACE

- GUARANTEE

- LIST OF DOCUMENTS ATTACHED

- TECHNICAL PARTICULARS

- VENDOR DRAWINGS & DOCUMENT  SCHEDULE

- IDENTIFICATION :

| S. NO. | ITEM NO. | DESCRIPTION | QTY | REMARKS |
| --- | --- | --- | --- | --- |
| 1.0 | 1545-E01 | 11kV Switch Board#01 | 1 Set |  |

- SCOPE :

This specification covers minimum requirements for the design, manufacture, assembly, testing at manufacturer’s works, packing and delivery at site of 11kV switchboard # 01 with complete accessories. This shall also include erection supervision, testing & commissioning and guarantees for operation of 11kV switchboard # 01 including minor modifications at site, for trouble free operation of Pashmina project, Orgadam, Sriperambudour taluk, Kancheepuram district, Tamil Nadu, approximate 50 kms from Chennai.

- CODES & STANDARDS :

Shall comply to latest editions of following relevant codes & standards, safety codes, Regulations of statutory Authorities (Chief Electrical Inspectorate to State Government).

IEC 282-1		MV HRC Fuse Links

IEC 644		MV HRC Fuse Links

IEC 60265-1		High voltage switches for rated voltages above 1KV & less than 52KV

IEC 60282-1		High voltage fuses – Current limting fuses

IEC 60269-1		Low voltage fuses – General requirements

IEC 60644		Specification for High voltage fuse links for motor circuit applications

IS : 5			Color for ready mixed paint & enamels

IS : 722		Specification for ac electricity meters

IS : 1248	Specification for direct acting indicating analog electrical measuring instruments & its accessories.

IS : 3427		Metal enclosed switchgear and control gear for voltages above 1000V but not exceeding 11000V.

IS : 5578		Guide for marking of insulated conductors.

IS : 9920		Switches and switch isolators for voltages above 1000V.

IS : 9921		AC Disconnectors and earth switches for voltage above 1000V.

IS : 2705		Specification for current transformers.

IS : 3156		Specification for voltage transformers.

IS : 3231		Specification for electrical relays for power system protection.

IS : 13118		Specification for high voltage alternating circuit breakers.

IS : 13703		Low voltage fuses for voltages not exceeding 1000V AC or 1500V DC.

IS :  5578 /IS 11353	Marking and arrangement of busbars.

--	Local statutory regulations,

--	Indian electricity rules 1956,

--	Indian electricity act-1910

--	Applicable codes and standards shall be the latest issue to the date of enquiry including addenda, revisions or supplements.

- SYSTEM PARTICULARS :

Power supply		: 11kV ± 10%, 50 Hz ± 3 %, 3 phase, 3 wire AC

Three Phase Symmetrical Fault Level	:		26.2 kA for 3 Sec.

Control supply

- Closing, tripping & indication	:	110V DC supply

- Space heater supply		:	230V, 50 HZ, 1PH, 3W

  - SITE ENVIRONMENTAL CONDITIONS :

5.1 	Design ambient temperature

(For Electrical Equipment)		: 	450 C

5.2	Relative humidity			: 	88% max, 77% min.

5.3	Altitude above mean sea level	: 	16 Mtrs.

5.4 	Monthly heaviest rainfall		:	143 mm

5.5	Monthly mean Wind speed		: 	10 KMPH

5.6 	Seismic zone				: 	Zone III

5.7 	Installation				:	Indoor-Pressurized Room

- CONSTRUCTION :

  - GENERAL REQUIREMENTS :

6.1.1	Switchboard shall be designed & constructed to facilitate inspection, cleaning, repair and maintenance and ensure absolute safety during operation, inspection and maintenance.

6.1.2	Each cable compartments shall have inspection cutout with suitable transparent sheet.	Suitable arrangement to be provided to carry out Thermography of cable compartment.

6.1.3	Terminal strip for outgoing control cables connections should be accessible to facilitate working and testing with breaker in test / service condition and while the switchgear is energized.

6.1.4	The draw out carriage on the switchgear shall have three positions - ‘Service’, ‘Test’ and ‘Draw Out’. Automatic safety shutters shall be provided to ensure the inaccessibility of all live parts after the breaker is drawn out. The outer door shall be pad lockable for safety. All circuit breaker trucks of the same rating shall be interchangeable. Suitable interlocks shall be provided to prevent faulty operation.

    - Selection sizing & suitability of all components shall be the vendor responsibility and all equipment required for safe and satisfactory operation shall be included by the vendor, even if it is not specifically mentioned.

6.1.6	All relays, meters and control components shall be mounted on the panel front only.

  - ENCLOSURE :

6.2.1	Enclosure shall be made of cold rolled sheet steel of adequate thickness not less than 2mm, assembled to form a rigid, freestanding, dead front structure. Vertical units shall be assembled to form a continuous line up of uniform height. Switchboard shall be totally enclosed dust and vermin proof. If necessary louvered openings with wire mesh shall be provided for natural ventilation. It shall be possible to extend the switchgear from both sides.

6.2.2	Neoprene gaskets shall be provided for all covers and openings. Minimum protection class for the enclosure shall be IP- 51.

6.2.3	Each cubicle shall be fully compartmentalized with metallic partitions having separate chambers for Main Bus bars, CT’s and Cable terminations, switching device, L.V. chamber for metering, protection and control equipment.

6.2.4	Independent pressure release flaps/vents shall be provided for each compartment.

6.2.5	All hardwares shall be corrosion resistant. All joints and connections of panel members shall be made by zinc passivated or cadmium plated high quality steel bolts, nuts & washers secured against loosening.

6.2.6	Suitable eyebolts for lifting of panel shall be provided. On removing the eye bolts no holes offering access to panel shall be permitted. Cable supporting facility shall be provided in cable alley for power and control cables.

  - BUSBARS :

6.3.1	Busbars shall be made of electrolytic grade copper “OR” aluminium as indicated in Technical particulars / Single line diagram (SLD) and shall be sleeved with Tracking Resistant material. Fiber glass/ metal sheet with cast resin bushing partitions shall be provided at every junction between two adjacent cubicles.

6.3.2	Busbar joints shall be provided with high tensile bots with spring washers. Prior to joining, oxide-inhibiting grease shall be applied after cleaning the surfaces. Joints shall be taped and shrouded.

6.3.3	Busbars shall extend through all units of the switchgear line up. Busbar cross section shall be selected based on the temperature rise indicated. Main busbar shall be of uniform cross-section and shall be sized to carry continuously the current specified in SLD. Feeder busbar shall be rated corresponding to breaker rating. Ground busbar (min 50x6 mm copper strip) shall run throughout the length of the switchgear. Busbars shall be provided with suitable color marking for phase identification.

6.3.4	Busbars shall be housed in a separate chamber. Wire guards / mesh shall be provided inside the sheeting to allow visual inspection of busbars / CT / PT / cable termination and to avoid accidental touch when rear cover is removed.

    - Busbars shall be supported at regular intervals and both busbars and the supports shall be adequately sized and braced to withstand the specified short circuit level without permanent deformation. All bus supports shall be of non- hygroscopic, flame retardant insulating supports.

  - GROUNDING :

All doors and movable parts shall be connected to ground bus with flexible stranded copper connections. Provision shall be made to connect the grounding busbar to the plant grounding grid at two ends. All non-current carrying metallic parts of the equipment shall be grounded.

  - ARRANGEMENT OF INTERNAL WIRING & TERMINATIONS :

6.5.1	The internal wiring for control, signaling, protection and instrument circuits shall be done with PVC insulated conductors, neatly tie wrapped together enclosed in plastic channels.

6.5.2	Conductors shall be terminated with adequately sized compression type lugs. Not more than one outgoing wire shall be connected per terminal. Terminal strips shall preferably be separated from power circuits by metal barriers or enclosures. All spare contacts of auxiliary relays, timers etc. shall be wired up to the terminals. Minimum 6 nos. spare terminals shall be provided on each terminal block.

6.5.3	Wiring shall be carried out with 1100 Volts grade. Each wire shall be identified at both ends by correctly numbered ferrules.

6.5.4	All internal control wiring shall be carried out by stranded insulated copper wires of 2.5 mm2 for power and current circuits and 1.5 mm2 for potential and all other control circuits.  Color Coding for internal panel wiring shall be as per vendor’s standard.

6.5.5	All inter panel control wiring shall be done by the switchgear vendor. Plugs provided should have scraping ground terminal. All shipping section of the panel shall have proper identification and ferruling for joining shipping section at site.

6.5.6	One AC & one DC control power supply feeder shall be made available by owner. The vendor shall arrange supply to each cubicle with individual isolation.

  - CABLE COMPARTMENT, CABLE  ENTRY AND TERMINATIONS :

6.6.1	Incoming & Outgoing power connection shall be through XLPE cables. Suitable termination arrangement shall be provided for number and size of cables as specified in Data sheets / SLD.

6.6.2	Cable entry shall be from bottom, ample space for connection of cables shall be provided at the rear of the switchboard. Cable lugs for power and control cable with requisite bushings for sealing power cable entries shall be included in the scope of supply of the switchgear.

    - The switchgear shall be supplied complete with supports for clamping incoming & outgoing cables. Terminal blocks shall not be used to support cables. The head room available between cable gland plate and terminal lug shall be sufficient so as to allow proper termination of cables.

    - The cable compartment shall be accessible from the rear of the cubicle and designed to accommodate the following equipment :-

- Current Transformers.

- Voltage Transformers

-	Cable-end Boxes.

6.7	LOW VOLTAGE COMPARTMENT :

6.7.1	In order to accommodate the protection relays, control and indicating equipment a separate compartment in the upper part of the cubicle front shall be provided.

6.7.2	All indicating equipment such as relays, ammeters etc. shall be mounted on the front door.  Auxiliary relays, fuses, CT terminals, MCB’s etc. shall be mounted and wired in the L.V. compartment.

6.7.3	Auxiliary contactors/relays/terminals shall be suitable for mounting on DIN rail.   Separate terminal blocks shall be considered for “Closing signals”, “Tripping signals”, “Auxiliary contacts”, “mA signals (if any)” etc.

6.8	Control circuits :

6.8.1	The equipment shall be designed in accordance with IEC standard recommendations to operate with an over voltage upto 10 % and under voltage upto 15 % except for the tripping and closing circuits.

6.8.2	The tripping circuit shall allow the operation with 70 % to 110 % of rated DC auxiliary voltage supply. The closing circuit shall allow the operation with 85 % to 110 % of rated DC or AC auxiliary voltage supply.

6.8.3	For the protection of the different circuits such as control voltage supply, charging motor, heater etc. applicable MCB's shall be provided individually for each cubicle circuit.

6.8.4	For receiving and distributing AC and DC power for control circuit suitable rated 2 pole MCB’s to be considered.

6.8.5	“MCB off” indicating lamp to be considered in case of MCB (DC) is “OFF”.

  - FAULT PROTECTIONS, ANNUNCIATION AND INTERLOCKS :

6.9.1	Each circuit breaker cubicle shall be provided with necessary protection relays as per SLD. Remote interlock & inter trip facility for all the incoming & outgoing circuit breakers shall be provided.

6.9.2 	Inter tripping facility shall be provided between the following panels :-

a) Power and motor control center #01 to 11kV Switchboard#01

b) Power and motor control center #02 to 11kV Switchboard#01

c) 11 kV Switchboard#01 to 11kV Outdoor Load Break Switch

    - Distribution transformer feeders shall be furnished with auxiliary relays for alarm and trip indications as shown in SLD. Each transformer feeders shall have provision to receive the following transformer fault alarm & trip contacts:-

a) 	Winding Temperature Alarm

b)	Winding Temperature Trip

c)	Buchholz Alarm

d)	Buchholz Trip

e)	Oil Temperature Alarm

f)	Oil Temperature Trip

g)	Magnetic Oil Gauge Alarm

The above trip & alarm contacts shall trip the transformer feeder & provide annunciation. Transformer feeder shall not be tripped in case of bus under voltage.

Two sets of Transformer fault annunciation contact from each feeder shall be wired to terminal block to be connected to the DCS / Down stream breaker panel.

6.9.4 	Static annunciation facility to be provided for each transformer outgoings as indicated in SLD. Twelve window annunciator with hooter shall be provided on each outgoing feeder for transformer fault alarms with provision for testing the annunciator window lamps and hooter. Push buttons for fault acknowledge, reset and lamp test shall be provided. Also four-window annuciator facility with in built push buttons shall be provided for each incomer for under voltage indication.

- ELECTRICAL EQUIPMENT & COMPONENT :

  - VACUUM CIRCUIT BREAKER :

Circuit Breaker shall be draw out type, trip free and shall have anti-pumping facilities. Breaker current ratings and short circuit ratings shall be as indicated in the SLD. Circuit breakers shall be designed with low switching over voltage level and long switching life.

The breakers shall have motor operated spring charged mechanism. It shall be possible to charge the springs manually, if required. Mechanical indication of spring position - charged/discharged shall be provided. In case the limit switch fails to cut out the spring charging motor when the springs are fully charged the motor shall be automatically de-coupled and annunciation for this shall be provided. Energy storage shall be sufficient for an open-close-open operation at rated capacity.

The breakers shall have 8 NO + 8 NC spare auxiliary contacts. If these are not available an auxiliary contactor shall be used to multiply the auxiliary contacts of the breakers. All auxiliary contacts shall be wired to the terminal block.

Each breaker shall be provided with an operation counter and mechanical ON – OFF indicator.

An integral earth switch system or separate earthing carriage shall be provided after withdrawing the circuit breaker, this can be inserted to facilitate grounding of cables.

Suitable electrical interlock along with audio / visual indication shall be provided to prevent closing of earthing truck on live busbars.

During circuit breaker truck withdrawal the shutters shall cover the branch bars automatically for circuit breaker connection.

The operation linkage for the earthing switch shall be incorporated in order to guarantee necessary interlock between earthing switch and circuit breaker. Integral Earthing switch shall be Triple pole and shall be installed in the cable compartment.

Circuit Breaker truck:

All the with drawable elements shall be mounted on a stable sheet steel construction in the same manner, as the cubicle’s front on which circuit breaker is mounted.

The truck shall be provided with three / four, large rollers, which allows it to be readily wheeled on all types of floors.

The arrangement of the contacts shall ensure extreme robustness and stability under fault conditions.

Mechanical interlocking shall be provided to fulfill the following functions:-

a)	To prevent the truck from being moved from the test to the service position or vice versa when the circuit breaker is closed.

b)	To prevent the closing of the circuit breaker while the truck is at any 	intermediate point between the test and locked in service position.

c)	The plug of the secondary wiring shall be automatically engaged when the 	truck is moved into the service position.

d)	In the reverse operation, the plug remains engaged until withdrawn by hand 	on the truck and it is removed from the cubicle.

  - INSTRUMENT TRANSFORMERS :

Current transformer, Potential transformer and measuring instruments to be provided by vendor as shown in attached SLD.

Current and voltage transformers shall be cast resin insulated. Primary and secondary terminals shall be marked distinctly.

    - Current Transformers (CT) :

Current Transformer shall be mounted on the switchgear stationary parts. The CT ratio & burden shall be as shown in the SLD.

a)	Accuracy class 1.0 for metering.

b)	Accuracy class 5P 20 for relays.

    - Potential Transformers (PT) :

The potential transformers shall be drawout type and provided with primary and secondary fuses. Burden and accuracy class shall be in accordance with the load requirements.  Burdens shall be selected to suit relay / Instrument loads selected by Vendor.

The drawout mechanism shall disconnect the busbars before the PT or its primary fuses become accessible.

  - MULTI FUNCTION METERS:

7.3.1	Multi function power meter shall be compact, suitable for panel mounting with high visibility LED display & provision for High/ Low limit alarms on selected measurements. Reading & retrieval of the recorded data shall be possible.

Units shall measure: -

a)	Voltage, Current, Frequency.

b)	Watts, VA, Power Factor, Var.

c)	Watt-hour, Var hour.

d)	Harmonics (Current & Voltage THD) etc.,

7.3.2	Multi Function Meter shall have: -

a)	Simultaneous 3-phase display.

b)	3-Line x 5-digit display.

c)	All measured quantities can be displayed using scroll function

7.3.3	All auxiliary equipment such as shunts, transducers, CT’s and PT’s that are required shall be included in the supply.

  - RELAYS :

Relays shall be draw out, microprocessor based flush mounting type fitted with dust tight covers. The relay shall be adjusted over a wide range to provide discrimination with devices having different characteristics. Non-protection relays can be of fixed type. Relays shall have ‘built in’ flags to indicate relay operation. It shall be possible to reset the flag without opening the relay case. The relays shall be suitable for 110 V, DC supply.

  - INDICATING LAMPS & PUSH BUTTONS :

Color coding of push buttons & indicating lamps shall be as follows:

| PUSH BUTTON |  | INDICATING LAMPS |  |
| --- | --- | --- | --- |
| Alarm Reset | Yellow | Running / ON | Green |
| Lamp Test | Green | Stop / OFF | Red |
| Trip circuit “healthy” check | Black | Fault / Auto trip | Amber |
|  |  | Spring Charged | White |
|  |  | Control power “healthy” | White |
|  |  | D.C. failure | Blue |

Low power consumption indicating lamps/LED shall be used with translucent lamp covers to diffuse light. Lamps shall be supplied complete with the necessary current limiting resistor.

  - CONTROL SWITCHES :

Each circuit breaker feeder shall be provided with Trip-Neutral-Close control switch.

All control switches shall be rotary, back connected type having a cam operated contact mechanism. Phosphor bronze contacts shall be used on the control switches. Circuit breaker control switches shall be 3-position spring return to neutral. They shall have ‘Pistol Grip’ handle. Number of ways, locking system, lost motion device, if required etc. shall be shown on the relevant schematic drawings. Two ‘spare’ ways shall be provided on these switches.

  - SPACE HEATERS AND ILLUMINATION :

Space heater for each cubicle / vertical panel shall be located at the bottom of the switchgear and shall be controlled through a thermostat with an adjustable setting and a manually operated switch. Provision shall be made for space heater circuit for all motors.

Panel shall be provided with interior lighting. Metering/Relay compartment shall be illuminated preferably with door operated switch by means of 11W Compact Fluorescent lamps. The lighting fixture shall be suitable for 230V, 50Hz, AC supply.

- MAKE OF COMPONENTS :

| SL.NO. | ITEM | MAKE |
| --- | --- | --- |
| 1 | Vacuum Circuit Breaker | ABB / SIEMENS / ALSTOM /EQ. |
| 2 | MV Fuse Links | ABB |
| 3 | Vacuum Bottles | WESTING HOUSE/TOSHIBA |
| 4 | Protective Relays | EASUN/ALSTOM/ABB/SIEMENS |
| 5 | Breaker Control Switch | ABB/EASUN ROYRALLE/ Equivalent |
| 6 | Digital Meters | ENERCON/AE/IMP/MECO |
| 7 | Auxiliary Relays | ABB/SIEMENS/GE/ALSTOM |
| 8 | Selector Switches | SIEMENS/L & T |
| 9 | Push Buttons & Indication Lamps | SIEMENS/L & T/RAAS CONTROLS |
| 10 | MCB | MDS/HAVELLS/INDO ASIAN |
| 11 | Current & Potential Transformer | INDCOIL/AE/KAPPA/PRECISE |

  - EQUIPMENT NAME PLATE:

Permanent non-corrosive nameplate with white background and black letters shall be fixed on the each compartment indicating item no and service description as shown on the SLD. The nameplate shall indicate the following:

First Line		:	Equipment Item No.

Second Line	:	Equipment description

Master nameplate shall be provided indicating as a minimum the switchgear volt, volt-ampere rating, short circuit rating, item number and manufacture’s name and model number.

Name Plate shall be provided on each equipment (PB’s, Indication Lamps, Auxiliary Relays, Selector Switches etc) those mounted on the Switchboard.

Listing and Labeling : The switchboard and all devices mounted thereon shall be listed and labeled for their intended use.

- PAINTING :

All metal surfaces shall be thoroughly cleaned and degreased to remove mill scale, rust, grease and dirt. Fabricated structures shall be pickled then rinsed to remove any trace of acid. The under surface shall be prepared by applying a coat of Phosphate paint and a coat of yellow Zinc Chromate primer. The under surface shall be free from all imperfections before undertaking the finishing coat.

After preparation of under coat, the Switchboard shall be spray painted with two coats of epoxy based final paint. The color shade of final paint shall be shade 631 (light grey) as per IS : 5. Spray painted finished panels shall be dried in stoving ovens in dust free atmosphere.

- INSPECTION AND TESTING :

- Equipment shall be tested and Inspected at manufacturer’s works before dispatch to ensure compliance with relevant specifications, drawings, Codes & Standards.

The Owner or his representatives may visit the works during manufacture of various equipment to access progress of work as well as to ascertain the Quality of raw materials used.

Owner shall be given minimum four weeks advance notice for witnessing the final testing. The minimum testing requirements for all components/ equipment shall confirm to the requirements stipulated in applicable codes & standards.

Tests shall be carried out at manufacturer’s works under his care & expense. All routine tests as specified in applicable standard codes shall be conducted:-

- Dimensional checks,

- Continuity checks,

- Component Rigidity checks,

- Insulation resistance checks,

- High Voltage tests Etc.

Type tests certificate for the similar type of Equipment shall be furnished along with the bids. Manufacturer shall submit separate quote for the Type tests.

- PACKING :

The panel shall be shipped to site packed in wooden crates suitable for Road/Rail transport. They shall be wrapped in polyethylene sheets before being placed in crates to prevent damage to the finish. Crates shall have skid bottoms for handling.

- SPECIAL TOOLS:

A set of special tools which are necessary or convenient for erection, commissioning, maintenance and overhauling of the equipment shall be included in the scope of supply.

The tools shall be shipped in separate containers, clearly marked with the name of the equipment for which they are intended.

14.0     SPARES:

The Bidder shall submit a list of recommended spare parts for two (2) years satisfactory and trouble free operation, indicating the itemized price of each item of the spares.

Also, required commissioning of spares shall be provided by seller free of cost.

- DEVIATIONS :

Any deviations from the requirements of this specification shall be stated as exceptions in Vendor / contractor’s proposal. Unless specific exceptions are stated, it shall be understood that the equipment is in complete accordance with the specification.

- QUALITY ASSURANCE :

Manufacturer shall follow his standard procedures for Quality Assurance and control. However, the standard procedures shall be submitted to the owner in extent of order.

The procedure shall be in such a form as to clearly delineate the manufacturing sequence and major inspection points and to reference manufacturer’s test and inspection procedures.

The owner will inform the manufacturer as to which of the Inspection points and tests will be witnessed.

- GUARANTEE :

D

Guarantee shall be for proper design, installation and workmanship. Vendor / contractor shall guarantee all performance parameters. The guarantee shall be for a period of 12 months from the date of commissioning or 18 months from the date of last supply whichever is earlier.

- LIST OF DOCUMENTS ATTACHED :

|  | SL. NO | DESCRIPTION | SPEC. NO. / DWG. NO. | NO. OF SHEETS | REV | REMARKS |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1.0 | Symbols for schematics and SLD & schematic wiring diagram symbols | 108001-9999-009 | 3 | 0 |  |
|  | 2.0 | SLD for 11kV Switchboard#01 | 408303-1545-009 | 1 | 0 |  |

- TECHNICAL PARTICULARS  (11KV SWITCHBOARD#01) :

| SL. NO. | DESCRIPTION | PURCHASER’S REQUIREMENT | BIDDER TO FILL IN |
| --- | --- | --- | --- |
| A | GENERAL : |  |  |
| 1.0 | Make | ABB / SIEMENS / ALSTOM |  |
| 2.0 | Enclosure | IP 51 |  |
| 3.0 | Type | Metal enclosed draw out type |  |
| 4.0 | Thickness of sheet metal | 2mm for load bearing members, doors & gland plates. 3 mm for base frame. |  |
| 5.0 | Cable entry | Bottom. |  |
| 6.0 | Highest / Nominal system voltage | 12 /11kV |  |
| 7.0 | Short circuit withstand capability of Switchboard including Busbars |  |  |
| 7.1 | Short time current rating | 26.2 kA for 3 sec |  |
| 7.2 | Rated making capacity & dynamic stability rating | 66.8 kA Peak |  |
| 8.0 | Insulation level |  |  |
| 8.1 | One minute power frequency | 28 kV |  |
| 8.2 | Impulse withstand voltage | 75 kVp |  |
| 9.0 | Paint shade | Shade 631 as per IS 5 |  |
| 10.0 | Overall Dimensions in mm | Vendor to specify |  |
| 11.0 | Overall weight of the Panel (Kgs) | Vendor to specify |  |
| 12.0 | Operational clearences |  |  |
| 12.1 | In front for withdrawal of truck | 1.5 Mtrs |  |
| 12.2 | At back of panel | 1.0 Mtrs |  |
| 13.0 | Accessories with cubicle |  |  |
| 13.1 | Panel illumination lamp with switch |  |  |
| 13.2 | Space heater | 230V, 1-Φ; 50HZ, AC heater with thermostat control switch |  |
| 13.3 | 3 pin socket with switch | To be provided |  |
| B | BUSBAR |  |  |
| 1.0 | Busbar Material | Electrolytic Copper |  |
| 2.0 | Busbar insulation | Flame retardant cast resin material |  |
| 3.0 | Support insulators | Flame retardant track-resistant polyester glass or porcelain |  |
| 4.0 | Continuous current rating | As specified in SLD |  |
| 5.0 | Busbar joints | Zinc passivated bolts & tinned surfaces and flexible connections if required |  |
| 6.0 | Shrouds | At all joints & tappings |  |
| 5.0 | Maximum temperature rise over ambient temperature of 45°C | 40°C |  |
| 7.0 | Ground Bus : Material / Size | Copper Flat (Min. 50x6 mm) |  |
| C | CIRCUIT BREAKER |  |  |
| 1.0 | Arc Extinction Medium | Vacuum |  |
| 2.0 | Highest / Nominal system voltage | 12 / 11 kV |  |
| 3.0 | Short time current rating | 26.2 kA for 3 sec |  |
| 4.0 | Rated making capacity & dynamic stability rating | 66.8 kA Peak |  |
| 5.0 | Insulation level |  |  |
| 5.1 | One minute power frequency | 28 kV |  |
| 5.2 | Impulse withstand voltage | 75 kVp |  |
| 6.0 | Operating duty | 0 - 0.3 sec – CO - 3 min - CO |  |
| 7.0 | Total break time | Less than 5 cycles |  |
| 8.0 | Operating mechanism |  |  |
| 8.1 | Type of closing | Spring charged stored energy – Manual independent closing |  |
| 8.2 | Method of closing | Manual and motor drive |  |
| 9.0 | Breaker accessories visible and accessible from outside with cubicle door closed | Indication for Breaker position TEST/SERVICE/ISOLATED Breaker ON/OFF, spring charged Mechanical trip pushbutton Earth switch ON/OFF position indicator |  |
| 10.0 | Breaker position counter | To be provided |  |
| 11.0 | No. of auxiliary contacts | 8 NO + 8 NC |  |
| 12.0 | Earthing truck | Built in off load earthing switch for each breaker and separate bus earthing switch with (Electro mechanical) interlock OR Earthing trucks for bus earthing and cable earthing with safety interlocks and visual indication |  |
| D | CURRENT TRANSFORMER : |  |  |
| 1.0 | Make | Reputed |  |
| 2.0 | Type / Class of insulation | Cast Resin, Bar primary |  |
| 3.0 | Class | 5P 20 for protection - for metering |  |
| E | POTENTIAL TRANSFORMER |  |  |
| 1.0 | Make | Reputed |  |
| 2.0 | Type / Insulation Class | Cast Resin / Bar primary |  |
| 3.0 | Rated voltage : Primary / Secondary | As per SLD |  |
| 4.0 | Accuracy class/ Rated Burden | As per SLD |  |
| F | RELAYS | As per SLD |  |
| 1.0 | Make | SIEMENS/ABB/GE/ALSTOM/EASUN |  |
| 2.0 | Type | Numerical type 110V DC |  |
| 3.0 | Control voltage | 110V DC |  |
| G | METERS | As per SLD |  |
| 1.0 | Make | AE/IMP/MECO/ENERCON |  |
| 2.0 | Type | Digital; flush mounting type |  |
| 3.0 | Size | 96 sq. mm |  |
| H | HEAT LOAD |  |  |
| 1.0 | Heat load per panel (kW) | Vendor to specify |  |
| 2.0 | Total heat load (kW) | Vendor to specify |  |

- VENDOR DRAWINGS & DOCUMENT REQUIREMENT SCHEDULE:

| FOLLOWING ENGINEERING DATA IS TO BE SUBMITTED BY THE VENDOR WITH OFFER AND AS PART OF PURCHASE ORDER. EQUIPMENT ITEM NO AND ENQUIRY/P O NO. TO BE CLEARLY MARKED ON ALL DRAWINGS / DATA. P/X = PRINT/XEROX S=SOFT COPY IN CD |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SR. |  |  | REQUIRED | REQUIRED AFTER P.O. |  |  |  |  |
| NO. | ENGINEERING DATA |  | WITH OFFER | FOR APPROVAL | CERTIFIED FINAL |  |  | REMARKS |
|  |  |  | P/X | P/X | P/X |  | S |  |
|  | GENERAL ARRANGEMENT DWG WITH DIMENSIONS & SPACE REQUIRED FOR OPERATION & MAINTAINANCE WITH CABLE ENTRY |  | 3 | 4 | 6 |  | 1 |  |
|  | MODULE SIZE WITH DIMENSIONS |  | - | 4 | 6 |  | 1 |  |
|  | FOUNDATION PLAN WITH STATIC & DYNAMIC LOADS INCLUDING FIXING DETAILS |  | - | 4 | 6 |  | 1 |  |
|  | ENCLOSURE PROTECTION DETAIL |  | - | - | - |  | - |  |
|  | SINGLE LINE DIAGRAMS |  | 3 | 4 | 6 |  | 1 |  |
|  | CONTROL SCHEMATIC DIAGRAMS WITH TERMINAL DETAIL |  | - | 4 | 6 |  | 1 |  |
|  | INTER PANEL INTERCONNECTION WIRING DIAGRAMS |  | - | 4 | 6 |  | 1 |  |
|  | BILL OF MATERIALS WITH MAKE OF COMPONENTS |  | 3 | 4 | 6 |  | 1 |  |
|  | DESIGN CALCULATIONS FOR BUSBAR SIZING (THERMAL & DYNAMIC) |  | - | 4 | 6 |  | 1 |  |
|  | APPROVAL FROM LOCAL AUTHORITY |  | 3 | - | - |  | - |  |
|  | TEST CERTIFICATES FOR ALL COMPONENTS AS APPLICABLE a) ROUTINE TEST b) TYPE TEST c) PERFORMANCE TEST |  | 3 | - | 6 |  | 6 |  |
|  | TECHNICAL CATALOGUE OF ALL THE COMPONENTS & LIST OF USERS |  | 3 | - | 6 |  | - |  |
|  | INSTALLATION MANUAL |  | - | - | 6 |  | - |  |
|  | OPERATION & INSTRUCTIONS MANUAL |  | - | - | 6 |  | - |  |
|  | MAINTENANCE MANUAL |  | - | - | 6 |  | - |  |
|  | LIST OF COMMISIONING SPARES |  | 3 | - | 3 |  | - |  |
|  | DEVIATIONS IF ANY |  | 3 | - | - |  | - |  |
|  | LIST OF SPECIAL TOOLS REQUIRED FOR OPERATION & MAINTENANCE |  | 3 | - | 3 |  | - |  |
|  | INSPECTION AND TEST REPORT |  | - | - | 6 |  | - |  |
|  | QUALITY ASSURANCE PLAN |  | 3 | 3 | - |  | - |  |
|  | CERTIFICATE OF CONFORMANCE |  | - | - | - |  | - |  |
| NOTES : - FINAL DOCUMENTS TO BE SUBMITED SEPARATELY IN A FOLDER FOR EACH ITEM. |  |  |  |  |  |  |  |  |
|  |  | VENDOR DOCUMENT REQUIREMENT AND SCHEDULE |  |  |  |  |  |  |
| CHEMTEX |  | FOR M.V. SWITCHBOARD |  |  |  | SPEC.NO.IP009-43-03-02 REV. 0 |  |  |