IP-009

PASHMINA PROJECT

ELECTRICAL DESIGN BASIS

MOMENTIVE PERFORMANCE MATERIALS

CHENNAI

    - 230V, 16A, 3pin SP&N+E shall be provided considering accessibility with 25 Meters cable length.

- ELECTRICAL EQUIPMENT

  - 11 KV OUTDOOR SWITCHYARD EQUIPMENTS

4.1.1	11 KV OUTDOOR LOAD BREAK SWITCH

a) Type				:  	Off load

b) Rated voltage 			: 	11KV ±10 %

c) Rated frequency			:	50 HZ ±3 %

d) Rated current 			:	400A

e) Short circuit level at 11kV 		:	13.1 KA (To be confirmed later)

  - EMERGENCY (STAND BY) DG SET

4.2.1 	GENERAL

a) 	Number of Generating Sets		: 	One OR Two

b) 	Service				: 	Standby

c)	Voltage				: 	415V

d)	Frequency 				:  	50 HZ ±3 %

e)	Fault Level				: 	Later

f) 	Change over Scheme (AMF /Manual): 	Auto mains failure

g)	Time within which power must be 	: 	Immediate

made available to essential loads

h) 	Sequences of motor starting		: 	Not required

Mode of operation

- Independent				: 	Yes

- Synchronised			: 	Momentary paralleling with Grid

k)	Neutral Grounding			: 	Solidly Grounded

l) 	Accoustic enclosure	 		: 	Required.

m) 	Export of Power to Grid		: 	Not Envisaged

n)	Future provision for Export of power	: 	Not Required

to Grid

4.2.2	ENGINE

a)	Speed of the engine			:	Later

b) 	Type of starting (Battery / Air)	: 	Battery

c) 	Type of Cooling of the Engine	: 	Radiator cooled

d) 	Type of Fuel Oil			:	HSD

e)	Storage of Fuel Oil			: 	990Litres capacity

f) 	Requirement of Utilities

- Cooling Water			: 	Required

- Maximum Rating of the Drive to be started on the DG set

- Rating KW				: 	Later

- Type of starting			: 	Later

- Whether the Drive is started with 	: 	Both

No Load or on Load

i) 	Time within which DG can be fully	: 	90 sec

loaded from the instant of starting

signal given

    - ALTERNATOR

a) 	Alternator capacity			: 	Present process Critical loads only

b)	Type of Excitation			: 	Brushless

c)	Suitability for parallel Operation	: 	Required

d)	Type of Cooling			: 	Air Cooled

e)	Type of enclosure			:	IP-23

f)	Temperature Detecting elements

- For Winding				; 	Later

- For Bearing				: 	Later

g)	Number of Bearings			:	As per Vendor’s recommendation

h)	Class of insulation 			: 	Class – F with temp. rise limited 									to class B

4.3	 DISTRIBUTION TRANSFORMER

a) Voltage Ratio at No Load			:	11./ 0.433kV

b) Spare Capacity considered		:	Operating load not beyond 80%

c) Tap Changer				: 	Off Circuit

d) Range of Tap Changing			:	 + 5% at 2.5 % per step.

e) Cooling					: 	ONAN

f) Termination

- Primary Termination			:	Cable

- Secondary termination		:	Bus duct

g) Neutral Ground Arrangement		: 	Solid grounding

h) Vector Group.				: 	Dyn 11

i) Special Accessories such as 		:	Required

MOG, WTI, OTI, Gas relay

j) Temperature rise of oil / winding   		:	50/550C (by oil / winding resp.)								over ambient temp.

k) Winding Material (Cu / Al)			:	Copper

l) Impedance with tolerance		:           As per IS

m) Painting			           		:           RAL 7032

4.4	LV BUSDUCT

a) Type & section				: 	Non-segregated – Air Insulated

b) Bus duct section				: 	Rectangular

c) Degree of protection			: 	Indoor : IP 54, Outdoor : IP55

d) Continuous rating of Busbars		: 	Later

e) Fault level		 			: 	Later

f) Voltage grade				: 	415 Volts

g) Busbar material				: 	RAL 7032

- Phase & Neutral			: 	Aluminium

- Earth Busbar				: 	Aluminium “OR” GI

h) Copper flexible connections		: 	PMCC end & Transformer end